## Baseline Description
ASHRAE 90.1 Prototype Building Modeling Specifications
Pacific Northwest National Laboratory, updated on 03-21-2014
| Item | Descriptions |  |  | Data Source | PNNL Review Comments | 90.1 Simulation Working Group Review Comments | Reviewer Summary Evaluation
Status: Good = Good enough. OK = Okay for now, but needs improvement. Update = Needs improvement right away. (Identify better alternative in Comments Column)
[8 empty] | Status | Comments
Program
| Vintage | NEW CONSTRUCTION
| Location (Representing 8 Climate Zones) | Zone 1A: Miami (very hot, humid) Zone 1B: Riyadh, Saudi Arabia (very hot, dry) Zone 2A: Houston (hot, humid) Zone 2B: Phoenix (hot, dry) Zone 3A: Memphis (warm, humid) Zone 3B: El Paso (warm, dry) Zone 3C: San Francisco (warm,marine) | Zone 4A: Baltimore (mild, humid) Zone 4B: Albuquerque (mild, dry) Zone 4C: Salem (mild, marine) Zone 5A: Chicago (cold, humid) Zone 5B: Boise (cold, dry) Zone 5C: Vancouver, BC (cold, marine) | Zone 6A: Burlington (cold, humid) Zone 6B: Helena (cold, dry) Zone 7: Duluth (very cold) Zone 8: Fairbanks (subarctic) | Selection of representative climates based on Briggs' paper | These 17 climate cities have been reviewed and confirmed by the 90.1 Simulation Working Group.
| Available fuel types | gas, electricity
| Building Type (Principal Building Function) | Multifamily
| Building Prototype | High-Rise Apartment
Form
| Total Floor Area (sq feet) | 84,360 (152 ft x 55.5 ft) |  |  | Reference: PNNL-16770: Analysis of Energy Saving Impacts of ASHRAE 90.1-2004 for the State of New York
Building shape
| Aspect Ratio | 2.75
| Number of Floors | 10 |  |  | 90.1 Envelope Subcommittee
| Window Fraction (Window-to-Wall Ratio) | South: 30%, East: 30%, North: 30%, West: 30% Average Total: 30% |  |  | Reference: Based on feedback from the National Multi-family Housing Council (NMHC)
| Window Locations | See image
| Shading Geometry | none
| Azimuth | non-directional |  |  |  | PNNL will rotate the entire building 90 degree and then average the energy use results. In this way, the prototype building will be orientation neutral.
| Thermal Zoning | Each floor has 8 apartments except ground floor (7 apartment and 1 lobby with equivalent apartment area) Total 8 apartments per floor with corridor in center. Zone depth is 25 ft for each apartment from side walls and each apt is 25' x 38' (950 ft²). |  |  | Reference: PNNL-16770: Analysis of Energy Saving Impacts of ASHRAE 90.1-2004 for the State of New York
| Floor to floor height (ft) | 10
| Floor to ceiling height (ft) | 10 (No drop-in ceiling plenum is modeled)
| Glazing sill height (ft) | 3 ft (14 ft wide x 4 ft high)
Architecture
Exterior walls
| Construction | Steel-Frame Walls (2X4 16IN OC) 0.4 in. Stucco+5/8 in. gypsum board + wall Insulation+5/8 in. gypsum board |  |  | Reference: PNNL-16770: Analysis of Energy Saving Impacts of ASHRAE 90.1-2004 for the State of New York Base Assembly from 90.1 Appendix A.
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | ASHRAE 90.1 Requirements |  |  | ASHRAE 90.1
| Dimensions | based on floor area and aspect ratio
| Tilts and orientations | vertical
Roof
| Construction | Built-up Roof: Roof membrane+Roof insulation+metal decking |  |  | Reference: PNNL-16770: Analysis of Energy Saving Impacts of ASHRAE 90.1-2004 for the State of New York Base Assembly from 90.1 Appendix A.
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | ASHRAE 90.1 Requirements Residential; Roofs, Insulation entirely above deck |  |  | ASHRAE 90.1
| Dimensions | based on floor area and aspect ratio
| Tilts and orientations | horizontal
Window
| Dimensions | based on window fraction, location, glazing sill height, floor area and aspect ratio
| Glass-Type and frame | Hypothetical window with a weighted U-factor and SHGC
| U-factor (Btu / h * ft2 * °F) | ASHRAE 90.1 Requirements Residential; Vertical Glazing |  |  | ASHRAE 90.1 | 1. SHGC: There is no SHGC requirement in 90.1-2004 in climate zone 8. However, 90.1-2004 requires a SHGC of 0.45 in zone 8. Need input from the SWG on the SHGC value in the 90.1-2004 baseline model. Should we use the same value as specified in 2007 version? 2. VLT: There are no VLT requirements in the 2004 or 2007 Standard. However, we understand that the analysis for the impact of daylight in 2010 Standard requires an established VLT. PNNL suggests to use the VLT factor in Table C.3.5 in 90.1-2004 as the baseline assumptions. PNNL expects that the Envelop Committee will provide us the VLT for a specific U-factor and SHGC requirement for the daylighting analysis. Need inputs from the Simulation WG. 3. Window Framing: 90.1-2007 requires the different U-factor for different window framing, which is not the case for the 2004 version. What is the general practice for the window framing type in a typical large office building? Nonmetal framing?
SHGC (all)
| Visible transmittance | Same as above requirements
| Operable area | 100%
Skylight
| Dimensions | Not Modeled
| Glass-Type and frame | NA
U-factor (Btu / h * ft2 * °F)
SHGC (all)
Visible transmittance
Foundation
| Foundation Type | Slab-on-grade floors (unheated)
| Construction | 8" concrete slab poured directly on to the earth
| Slab on grade floor insulation Level (F-factor) | ASHRAE 90.1 Requirements |  |  | ASHRAE 90.1
| Dimensions | based on floor area and aspect ratio
Interior Partitions
| Construction | 2 x 4 uninsulated stud wall
| Dimensions | based on floor plan and floor-to-floor height
| Internal Mass | 8 lbs/ft2 of floor area |  |  | Reference: Building America Research Benchmark
Air Barrier System
| Infiltration (ACH) | 0.2016 cfm/ft² of gross exterior wall area at all times (at 10 mph wind speed) |  |  | Reference: PNNL-18898. Infiltration Modeling Guidelines for Commercial Building Energy Analysis. | The Standards (90.1-2004 or 2007) do not specify air infiltration rates. This simple assumption is common practice in building energy modeling but probably underestimates the real impact of infiltration. We need to discuss the reasonable assumption of infiltration rate to model in the baseline building. More importantly, how do we handle the 0.4 cfm/ft² air leakage rate (at 75 pa) as specified in the recently approved addenda z to 90.1-2007?
HVAC
System Type
| Heating type | Water Source Heat Pumps |  |  | 90.1 Mechanical Subcommittee
Cooling type
| Distribution and terminal units | Constant volume
HVAC Sizing
| Air Conditioning | autosized to design day |  |  |  | Design day refers to ASHRAE's design day data as 99.6% for heating and 0.4% for cooling conditions.
| Heating | autosized to design day
HVAC Efficiency
| Air Conditioning | ASHRAE 90.1 Requirements Minimum Equipment Efficiency for Electrically Operated Unitary and Applied Heat Pumps |  |  | ASHRAE 90.1 | For this apt model, we assume that the units would likely be single phase and would use the NAECA efficiencies at 13 SEER as the baseline efficiency. However, the minimum efficiency requirement as printed and published in 90.1-2004 is 12 SEER. Need direction from the SWG.
Heating
HVAC Control
| Thermostat Setpoint | 75°F Cooling/70°F Heating |  |  |  | The current model doesn't have thermostat setback. Would this a common practice to assume the thermostat setback in apartment buildings? PNNL's study for a mid-rise apt in Boston shows the setback practice. Reference: PNNL-15997. Building Energy Model Calibration for Maverick Gardens Mid-Rise A
| Thermostat Setback | No setback for apartments
| Supply air temperature | Maximum 110F, Minimum 52F
| Economizers | ASHRAE 90.1 Requirements |  |  | ASHRAE 90.1
| Ventilation | ASHRAE Ventilation Standard 62.1 See under Outdoor Air |  |  | ASHRAE Ventilation Standard 62.1
| Demand Control Ventilation | ASHRAE 90.1 Requirements |  |  | ASHRAE 90.1
| Energy Recovery | ASHRAE 90.1 Requirements |  |  | ASHRAE 90.1
Supply Fan
| Fan schedules | See under Schedules
| Supply Fan Total Efficiency (%) | Depending on the fan motor size |  |  | ASHRAE 90.1 requirements for motor efficiency and fan power limitation | Building America Benchmark suggests using 0.55 watts/cfm for fan power consumption in residential buildings. If assuming the fan total efficiency is 58%, the corresponding fan pressure drop is 1.5 in. w.c., which seems reasonable for this application.
| Supply Fan Pressure Drop | Depending on the fan supply air cfm
Service Water Heating
| SWH type | Central Water Heater with Storage Tank
| Fuel type | Natural Gas |  |  | Reference: PNNL 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Thermal efficiency (%) | ASHRAE 90.1 Requirements |  |  | ASHRAE 90.1
| Tank Volume (gal) | 600 (central) |  |  | Reference: PNNL 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Water temperature setpoint | 140 F
| Water consumption | See under Schedules |  |  | Reference: Building America Research Benchmark
Internal Loads & Schedules
Lighting
| Average power density (W/ft2) | Apartment units: 0.36 W/ft² (daily peak for hard-wired lighting) and 0.09 W/ft² (daily peak for plug-in lighting) - See under Lighting Load for the detailed calculations. Corridor: 0.5 W/ft² |  |  | Apartment: Building America Research Benchmark Corridor: 90.1-2004 | The 0.7 W/ft2 value for multi-daily building in 90.1-2004 is for building common area only (hallway, recreational center, etc.), permanent living spaces are not regulated. Therefore, PNNL suggests using the hard-wired lighting loads specified by Building America Benchmark. PNNL will work with Lighting Committee for inputs.
| Schedule | See under Schedules |  |  | Reference: Building America Research Benchmark
| Daylighting Controls | ASHRAE 90.1 Requirements |  |  | ASHRAE 90.1
| Occupancy Sensors | ASHRAE 90.1 Requirements |  |  | ASHRAE 90.1
Plug load
| Average power density (W/ft2) | 0.62 W/ft² daily peak per apartment, including all the home appliances See under Plug Load for the detailed calculations |  |  | Reference: Building America Research Benchmark
| Schedule | See under Schedules
Occupancy
| Average people | See under Zone Summary |  |  | Reference: Building America Research Benchmark | Assuming averagely two-bedroom for each apartment for the entire building. Number of occupants per unit = 0.5 × Nbr + 1.5
| Schedule | See under Schedules
Misc.
Elevator
| Quantity |  | 1 |  | Reference: DOE Commercial Reference Building Models of the National Building Stock
| Motor type |  | Traction
| Peak Motor Power (watts/elevator) |  | 20370
| Heat Gain to Building |  | Interior
| Peak Fan/lights Power (watts/elevator) |  | 161.9 |  | 90.1 Mechanical Subcommittee, Elevator Working Group | PNNL suggests to add elevator energy use.
| Motor and fan/lights Schedules |  | See under Schedules |  | Reference: DOE Commercial Reference Building Models of the National Building Stock
Exterior Lighting
| Peak Power (W) | 13580 |  |  | ASHRAE 90.1 | PNNL suggests to model the exterior lighting. Need input from the experts in the Lighting Committee.
| Schedule | See under Schedules
References
Briggs, R.S., R.G. Lucas, and Z.T. Taylor. 2003. Climate Classification for Building Energy Codes and Standards: Part 2—Zone Definitions, Maps, and Comparisons. ASHRAE Transactions 109(2).
Gowri K, MA Halverson, and EE Richman. 2007. Analysis of Energy Saving Impacts of ASHRAE 90.1-2004 for New York. PNNL-16770, Pacific Northwest National Laboratory, Richland, WA. http://www.pnl.gov/main/publications/external/technical_reports/PNNL-16770.pdf
Gowri K, DW Winiarski, and RE Jarnagin. 2009. Infiltration modeling guidelines for commercial building energy analysis . PNNL-18898, Pacific Northwest National Laboratory, Richland, WA. http://www.pnl.gov/main/publications/external/technical_reports/PNNL-18898.pdf
Building America Research Benchmark. http://www1.eere.energy.gov/buildings/building_america/index.html
DOE Commercial Reference Building Models of the National Building Stock: http://www.nrel.gov/docs/fy11osti/46861.pdf
RECS 2005. EIA's Residential Energy Consumption Survey. http://www.eia.doe.gov/emeu/recs/
PNNL. 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models. Pacific Northwest National Laboratory, Richland, Washington. Available at https://www.energycodes.gov/development/commercial/90.1_models.

## Zone Summary
Zone Summary
Zone1 | Area (ft²) | Conditioned (Y/N) | Volume (ft³) | Multipliers | Gross Wall Area (ft²) | Window Glass Area (ft²) | Lighting (W/ft²) | People (ft²/person) | Number of People | Plug and Process (W/ft²)
G SW APARTMENT | 950 | Yes | 9498.6755 | 1 | 629.9093 | 189 | 0.3511 | 379.9692 | 2.5002 | 0.61966
G NW APARTMENT | 950 | Yes | 9498.6755 | 1 | 629.9093 | 189 | 0.3511 | 379.9692 | 2.5002 | 0.61966
OFFICE | 950 | Yes | 9498.6755 | 1 | 629.9093 | 189 | 1.1011 | 949.923 | 1.0001 | 0.61966
G NE APARTMENT | 950 | Yes | 9498.6755 | 1 | 629.9093 | 189 | 0.3511 | 379.9692 | 2.5002 | 0.61966
G N1 APARTMENT | 950 | Yes | 9498.6755 | 1 | 379.9692 | 114 | 0.3511 | 379.9692 | 2.5002 | 0.61966
G N2 APARTMENT | 950 | Yes | 9498.6755 | 1 | 379.9692 | 114 | 0.3511 | 379.9692 | 2.5002 | 0.61966
G S1 APARTMENT | 950 | Yes | 9498.6755 | 1 | 379.9692 | 114 | 0.3511 | 379.9692 | 2.5002 | 0.61966
G S2 APARTMENT | 950 | Yes | 9498.6755 | 1 | 379.9692 | 114 | 0.3511 | 379.9692 | 2.5002 | 0.61966
M SW APARTMENT | 950 | Yes | 9498.6755 | 8 | 629.9093 | 189 | 0.3511 | 379.9692 | 2.5002 | 0.61966
M NW APARTMENT | 950 | Yes | 9498.6755 | 8 | 629.9093 | 189 | 0.3511 | 379.9692 | 2.5002 | 0.61966
M SE APARTMENT | 950 | Yes | 9498.6755 | 8 | 629.9093 | 189 | 0.3511 | 379.9692 | 2.5002 | 0.61966
M NE APARTMENT | 950 | Yes | 9498.6755 | 8 | 629.9093 | 189 | 0.3511 | 379.9692 | 2.5002 | 0.61966
M N1 APARTMENT | 950 | Yes | 9498.6755 | 8 | 379.9692 | 114 | 0.3511 | 379.9692 | 2.5002 | 0.61966
M N2 APARTMENT | 950 | Yes | 9498.6755 | 8 | 379.9692 | 114 | 0.3511 | 379.9692 | 2.5002 | 0.61966
M S1 APARTMENT | 950 | Yes | 9498.6755 | 8 | 379.9692 | 114 | 0.3511 | 379.9692 | 2.5002 | 0.61966
M S2 APARTMENT | 950 | Yes | 9498.6755 | 8 | 379.9692 | 114 | 0.3511 | 379.9692 | 2.5002 | 0.61966
T SW APARTMENT | 950 | Yes | 9498.6755 | 1 | 629.9093 | 189 | 0.3511 | 379.9692 | 2.5002 | 0.61966
T NW APARTMENT | 950 | Yes | 9498.6755 | 1 | 629.9093 | 189 | 0.3511 | 379.9692 | 2.5002 | 0.61966
T SE APARTMENT | 950 | Yes | 9498.6755 | 1 | 629.9093 | 189 | 0.3511 | 379.9692 | 2.5002 | 0.61966
T NE APARTMENT | 950 | Yes | 9498.6755 | 1 | 629.9093 | 189 | 0.3511 | 379.9692 | 2.5002 | 0.61966
T N1 APARTMENT | 950 | Yes | 9498.6755 | 1 | 379.9692 | 114 | 0.3511 | 379.9692 | 2.5002 | 0.61966
T N2 APARTMENT | 950 | Yes | 9498.6755 | 1 | 379.9692 | 114 | 0.3511 | 379.9692 | 2.5002 | 0.61966
T S1 APARTMENT | 950 | Yes | 9498.6755 | 1 | 379.9692 | 114 | 0.3511 | 379.9692 | 2.5002 | 0.61966
T S2 APARTMENT | 950 | Yes | 9498.6755 | 1 | 379.9692 | 114 | 0.3511 | 379.9692 | 2.5002 | 0.61966
T CORRIDOR2 | 836 | No | 8358.7073 | 1 | 110.0081 | 24.0037 | 0.5516 | 0 | 0 | 24.56
G CORRIDOR | 836 | No | 8358.7073 | 1 | 110.0081 | 24.0037 | 0.5516 | 0 | 0 | 0
M CORRIDOR | 836 | No | 8358.7073 | 8 | 110.0081 | 24.0037 | 0.5516 | 0 | 0 | 0
TOTAL3 | 84360 |  | 843481.1175 |  | 41495.22 | 12360.0372 |  |  | 198.5161
AREA WEIGHTED AVERAGE | [6 empty] | 0.37941 | 348.733 |  | 0.80164
1. Each apartment zone contains one apartment with one bedroom, living room and bathroom.
2. Elevator load is added in the top floor corridor zone.
3. Only volume, and gross wall area include unconditioned space.

## Outdoor Air
Minimum Outdoor Ventilation Air Requirements
|  |  |  | Total Occupants | Total OSA Ventilation (cfm/zone) |  |  | Total OSA Ventilation (cfm/ft2)
Zone | Area (ft2) | Multipliers | Assumed Space Type | 62.1-2004 | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007) | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007)
G SW APARTMENT | 950 | 1 | Residential single bedroom apartment | 2 | 55 | 55 | 55 | 0.057895 | 0.057895 | 0.057895
G NW APARTMENT | 950 | 1 | Residential single bedroom apartment | 2 | 55 | 55 | 55 | 0.057895 | 0.057895 | 0.057895
OFFICE | 950 | 1 | Office space | 4.75 | 95 | 80.75 | 80.75 | 0.1 | 0.085 | 0.085
G NE APARTMENT | 950 | 1 | Residential single bedroom apartment | 2 | 55 | 55 | 55 | 0.057895 | 0.057895 | 0.057895
G N1 APARTMENT | 950 | 1 | Residential single bedroom apartment | 2 | 55 | 55 | 55 | 0.057895 | 0.057895 | 0.057895
G N2 APARTMENT | 950 | 1 | Residential single bedroom apartment | 2 | 55 | 55 | 55 | 0.057895 | 0.057895 | 0.057895
G S1 APARTMENT | 950 | 1 | Residential single bedroom apartment | 2 | 55 | 55 | 55 | 0.057895 | 0.057895 | 0.057895
G S2 APARTMENT | 950 | 1 | Residential single bedroom apartment | 2 | 55 | 55 | 55 | 0.057895 | 0.057895 | 0.057895
M SW APARTMENT | 950 | 8 | Residential single bedroom apartment | 2 | 55 | 55 | 55 | 0.057895 | 0.057895 | 0.057895
M NW APARTMENT | 950 | 8 | Residential single bedroom apartment | 2 | 55 | 55 | 55 | 0.057895 | 0.057895 | 0.057895
M SE APARTMENT | 950 | 8 | Residential single bedroom apartment | 2 | 55 | 55 | 55 | 0.057895 | 0.057895 | 0.057895
M NE APARTMENT | 950 | 8 | Residential single bedroom apartment | 2 | 55 | 55 | 55 | 0.057895 | 0.057895 | 0.057895
M N1 APARTMENT | 950 | 8 | Residential single bedroom apartment | 2 | 55 | 55 | 55 | 0.057895 | 0.057895 | 0.057895
M N2 APARTMENT | 950 | 8 | Residential single bedroom apartment | 2 | 55 | 55 | 55 | 0.057895 | 0.057895 | 0.057895
M S1 APARTMENT | 950 | 8 | Residential single bedroom apartment | 2 | 55 | 55 | 55 | 0.057895 | 0.057895 | 0.057895
M S2 APARTMENT | 950 | 8 | Residential single bedroom apartment | 2 | 55 | 55 | 55 | 0.057895 | 0.057895 | 0.057895
T SW APARTMENT | 950 | 1 | Residential single bedroom apartment | 2 | 55 | 55 | 55 | 0.057895 | 0.057895 | 0.057895
T NW APARTMENT | 950 | 1 | Residential single bedroom apartment | 2 | 55 | 55 | 55 | 0.057895 | 0.057895 | 0.057895
T SE APARTMENT | 950 | 1 | Residential single bedroom apartment | 2 | 55 | 55 | 55 | 0.057895 | 0.057895 | 0.057895
T NE APARTMENT | 950 | 1 | Residential single bedroom apartment | 2 | 55 | 55 | 55 | 0.057895 | 0.057895 | 0.057895
T N1 APARTMENT | 950 | 1 | Residential single bedroom apartment | 2 | 55 | 55 | 55 | 0.057895 | 0.057895 | 0.057895
T N2 APARTMENT | 950 | 1 | Residential single bedroom apartment | 2 | 55 | 55 | 55 | 0.057895 | 0.057895 | 0.057895
T S1 APARTMENT | 950 | 1 | Residential single bedroom apartment | 2 | 55 | 55 | 55 | 0.057895 | 0.057895 | 0.057895
T S2 APARTMENT | 950 | 1 | Residential single bedroom apartment | 2 | 55 | 55 | 55 | 0.057895 | 0.057895 | 0.057895
T CORRIDOR | 836 | 1 | Corridors (public spaces) | 0 | 41.8 | 50.16 | 50.16 | 0.05 | 0.06 | 0.06
G CORRIDOR | 836 | 1 | Corridors (public spaces) | 0 | 41.8 | 50.16 | 50.16 | 0.05 | 0.06 | 0.06
M CORRIDOR | 836 | 8 | Corridors (public spaces) | 0 | 41.8 | 50.16 | 50.16 | 0.05 | 0.06 | 0.06
TOTAL | 84360 |  |  | 162.75 | 4858 | 4927.35 | 4927.35 | 5.1737 | 5.2587 | 5.2587
1. Each apartment zone contains one apartment with one bedroom, living room and bathroom.
Residential single bedroom apartment
Corridors (public spaces)
Office space

## Plug Load
Annual Appliance and Equipment Loads for Apartment (Source: Building America Research Benchmark)
Appliance | Electricity (kWh/yr) | Natural Gas (therms/yr) | Sensible Load Fraction | Latent Load Fraction | Apartment Electricity (kWh/yr)
Refrigerator | 669 |  | 1 | 0 | 669
Clothes Washer (3 ft3 drum) | 52.5 + 17.5 x Nbr |  | 0.8 | 0 | 87.5
Clothes Dryer (Electric) | 418 + 139 x Nbr |  | 0.15 | 0.05 | 696
Clothes Dryer (Gas) | 38 + 12.7 x Nbr | 26.5 + 8.8 x Nbr1.00 (Electric) | 0.10 (Gas) 0.0 (Electric) | 0.00 (Electric) 0.05 (Gas) | NA
Dishwasher (8 place settings) | 103 + 34.3 x Nbr |  | 0.6 | 0.15 | 171.6
Range (Electric) | 302 + 101 x Nbr |  | 0.4 | 0.3 | 504
Range (Gas) |  | 22.5 + 7.5 x Nbr | 0.3 | 0.2
Plug-In Lighting | 0.2*(FFA * 0.8 + 455) |  | 1 | 0 | 243
Variable Miscellaneous Electric Loads (see under MEL) | 1231 +194 x Nbr+ 0.316 x FFA |  | 0.81 | 0.02 | 1045.5937
Fixed Miscellaneous Loads (Gas/Electric) | 360 | 11.5 | 0.13 | 0.25 | NA
Fixed Miscellaneous Loads (All-Electric) | 697 |  | 0.13 | 0.25 | NA
|  |  |  | Total kWh/yr | 3416.6937
|  |  |  | Daily Peak watts/ft² | 0.62364
Nbr: number of bedrooms | 2
FFA: finished floor area, ft² | 950

## Lighting Load
Lighting Load Calculation Assumptions (Reference - Hendron R. 2008. Building America Research Benchmark Definition. TP-550-44816, National Renewable Energy Laboratory, Golden, Colorado)
(available at - http://apps1.eere.energy.gov/buildings/publications/pdfs/building_america/44816.pdf)
Annual Hard-Wired Indoor Lighting kWh = (455 + 0.8 x CFA)*0.8
Annual Plug-in Indoor Lighting kWh = (455 + 0.8 x CFA)*0.2
CFA = | 950 | ft2 | per apartment unit
Per Apartment Unit
| Annual hard-wired lighting |  |  | 972 | kW
| Lighting use per day |  |  | 2663.0137 | W
| Peak lighting use |  |  | 341.4103 | W
| Annual hard-wired lighting |  |  | 243 | kW
| Lighting use per day |  |  | 665.75 | W
| Peak lighting use |  |  | 85.35 | W
Eplus Lighting input
|  |  | LPD (hard-wired) = | 0.35938 | W/ft2
|  |  | LPD (plug-in) = | 0.09 | W/ft2

## MEL
Benchmark Annual Energy Consumption for Miscellaneous Electric and Gas Loads. (three-bedroom house 1920 ft2)
Miscellaneous Electric Load | Avg. Units/ Household | Energy/ Unit kWh/yr | Energy/ Household kWh/yr
Hard-Wired
Fan (Ceiling) | 1.4 | 50 | 70
Air Handler Standby Losses | 0.8 | 67.2 | 53.76
HVAC Controls | 1 | 20.3 | 20.3
Home Security System | 0.187 | 195.1 | 36.4837
Ground Fault Circuit Interrupter | 3.85 | 6.2 | 23.87
Sump Pump | 0.099 | 40 | 3.96
Heat Lamp | 0.01 | 13 | 0.13
Garage Door Opener | 0.266 | 35 | 9.31
Carbon Monoxide Detector | 0.26 | 17.5 | 4.55
Smoke Detectors | 0.84 | 3.5 | 2.94
Garbage Disposal | 0.404 | 10 | 4.04
Doorbell | 0.67 | 44 | 29.48
Home Entertainment
First Color TV | 0.986 | 215.5 | 212.483
Second Color TV | 0.669 | 112.7 | 75.3963
Third Color TV | 0.296 | 66.7 | 19.7432
Fourth Color TV | 0.104 | 52.1 | 5.4184
Fifth or More Color TV | 0.028 | 45.8 | 1.2824
First VCR | 0.876 | 71.3 | 62.4588
Second VCR | 0.32 | 68.9 | 22.048
Third or More VCR | 0.072 | 68.6 | 4.9392
DVD Player | 0.472 | 50.1 | 23.6472
Video Gaming System | 0.631 | 20.4 | 12.8724
Clock Radio | 1.26 | 14.9 | 18.774
Boom box / Portable Stereo | 0.67 | 16.8 | 11.256
Compact Stereo | 0.46 | 112.3 | 51.658
Component / Rack Stereo | 0.73 | 153 | 111.69
Power Speakers | 0.296 | 24.4 | 7.2224
Subwoofer | 0.099 | 68.3 | 6.7617
Radio | 0.493 | 9.1 | 4.4863
Equalizer | 0.049 | 14.7 | 0.7203
Satellite Dish Box | 0.202 | 131.7 | 26.6034
Cable Box | 0.637 | 152.7 | 97.2699
Kitchen
Microwave | 0.933 | 135.1 | 126.0483
Freezer | 0.323 | 935 | 302.005
Extra Refrigerator | 0.179 | 1100 | 196.9
Coffee Maker (Drip) | 0.685 | 99.3 | 68.0205
Coffee Maker (Percolator) | 0.167 | 65 | 10.855
Toaster Oven | 0.345 | 50 | 17.25
Toaster | 0.837 | 43.7 | 36.5769
Waffle Iron | 0.325 | 25 | 8.125
Blender | 0.788 | 7 | 5.516
Can Opener | 0.65 | 3 | 1.95
Electric Grill | 0.01 | 180 | 1.8
Hand Mixer | 0.877 | 2 | 1.754
Electric Griddle | 0.256 | 6 | 1.536
Popcorn Popper | 0.305 | 5 | 1.525
Espresso Machine | 0.069 | 19 | 1.311
Instant Hot-water Dispenser | 0.006 | 160 | 0.96
Hot Plate | 0.236 | 30 | 7.08
Food Slicer | 0.414 | 1 | 0.414
Electric Knife | 0.374 | 1 | 0.374
Broiler | 0.01 | 80 | 0.8
Deep Fryer | 0.148 | 20 | 2.96
Bottled Water | 0.01 | 300 | 3
Trash Compactor | 0.01 | 50 | 0.5
Slow Cooker / Crock Pot | 0.581 | 16 | 9.296
Home Office
Laptop PC (Plugged In) | 0.152 | 47 | 7.144
Desktop PC w/ Speakers | 0.592 | 143.9 | 85.1888
PC Monitor | 0.592 | 119.8 | 70.9216
Printer (Laser) | 0.049 | 92.5 | 4.5325
Printer (Inkjet) | 0.118 | 39 | 4.602
Dot Matrix Printer | 0.03 | 115 | 3.45
DSL/Cable Modem | 0.2 | 17.6 | 3.52
Scanner | 0.05 | 49 | 2.45
Copy Machine | 0.02 | 25 | 0.5
Fax Machine | 0.03 | 326.3 | 9.789
Bathroom
Hair Dryer | 0.837 | 0.6 | 0.5022
Curling Iron | 0.532 | 1 | 0.532
Electric Shaver | 0.47 | 12.8 | 6.016
Electric Toothbrush Charger | 0.118 | 19.3 | 2.2774
Garage & Workshop
Auto Block Heater | 0.019 | 250 | 4.75
Lawn Mower (Electric) | 0.059 | 42.9 | 2.5311
Heat Tape | 0.03 | 100 | 3
Kiln | 0.02 | 50 | 1
Pipe and Gutter Heaters | 0.01 | 53 | 0.53
Shop Tools | 0.13 | 26.4 | 3.432
Other
Humidifier | 0.15 | 100 | 15
Water Bed | 0.066 | 1068 | 70.488
Sm. Freshwater Aquarium (5-20 gal) | 0.024 | 105 | 2.52
Md. Freshwater Aquarium (20-40 gal) | 0.024 | 180 | 4.32
Lg. Freshwater Aquarium (40-60 gal) | 0.024 | 340 | 8.16
Small Marine Aquarium (5-20 gal) | 0.002 | 245 | 0.49
Medium Marine Aquarium (20-40 gal) | 0.002 | 615 | 1.23
Large Marine Aquarium (40-60 gal) | 0.002 | 740 | 1.48
Vacuum Cleaner (Upright) | 0.946 | 31 | 29.326
Clock | 0.956 | 26 | 24.856
Cordless Phone | 0.601 | 23.2 | 13.9432
Cell Phone Charger | 0.45 | 77.4 | 34.83
Electric Blanket | 0.286 | 120 | 34.32
Answering Machine | 0.65 | 33.5 | 21.775
Battery Charger | 0.437 | 14.8 | 6.4676
Fan (Portable) | 0.946 | 11.3 | 10.6898
Air Cleaner | 0.217 | 65.7 | 14.2569
Vacuum Cleaner (Cordless) | 0.207 | 36.5 | 7.5555
Heating Pads | 0.67 | 3 | 2.01
Surge Protector / Power Strip | 0.36 | 3.9 | 1.404
Timer (Lighting) | 0.28 | 20.1 | 5.628
Timer (Irrigation) | 0.05 | 45.2 | 2.26
Iron | 0.847 | 53 | 44.891
Baby Monitor | 0.1 | 22.8 | 2.28
Fixed MELs |  |  | 2418.9609
Pool Heater (Electric) | 0.004 | 2300
Pool Pump (Electric) | 0.066 | 2228.3
Hot Tub / Spa Heater (Electric) | 0.056 | 1704
Hot Tub / Spa Pump (Electric) | 0.094 | 460
Well Pump (Electric) | 0.129 | 400
Coral Reef Aquarium (Electric) | 0.001 | 4500
Gas Fireplace | 0.035 | 1760
Gas Grill | 0.029 | 879
Gas Lighting | 0.005 | 557
Pool Heater (Gas) | 0.024 | 6506
Hot Tub / Spa Heater (Gas) | 0.038 | 2374
Other | 1 | 9.4

## Schedules
Apartment |  | 1 am | 2 am | 3 am | 4 am | 5 am | 6 am | 7 am | 8 am | 9 am | 10 am | 11 am | Noon | 1 pm | 2 pm | 3 pm | 4 pm | 5 pm | 6 pm | 7 pm | 8 pm | 9 pm | 10 pm | 11 pm | 12 pm
Source: Building America Benchmark/PTAC Rulemaking
People | ALL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85246 | 0.39344 | 0.2459 | 0.2459 | 0.2459 | 0.2459 | 0.2459 | 0.2459 | 0.2459 | 0.29508 | 0.52459 | 0.86885 | 0.86885 | 0.86885 | 1 | 1 | 1
Lighting | ALL | 0.066667 | 0.066667 | 0.066667 | 0.066667 | 0.18672 | 0.39363 | 0.43955 | 0.39272 | 0.1724 | 0.11901 | 0.11901 | 0.11901 | 0.11901 | 0.11901 | 0.11901 | 0.2059 | 0.43858 | 0.61644 | 0.82902 | 0.98584 | 1 | 0.69178 | 0.38357 | 0.16003
Plug | All | 0.45399 | 0.41104 | 0.39264 | 0.38037 | 0.38037 | 0.42945 | 0.53988 | 0.65031 | 0.66258 | 0.67485 | 0.68712 | 0.69939 | 0.68712 | 0.66258 | 0.65031 | 0.68098 | 0.80368 | 1 | 1 | 0.92638 | 0.88957 | 0.84663 | 0.71166 | 0.57669
Infiltration | ALL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Cooling | ALL | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Heating | ALL | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
SWH | ALL | 0.078431 | 0.039216 | 0.0098062 | 0.0098062 | 0.039216 | 0.27451 | 0.94118 | 1 | 0.96078 | 0.84314 | 0.76471 | 0.60784 | 0.52941 | 0.47059 | 0.41176 | 0.47059 | 0.54902 | 0.72549 | 0.86275 | 0.82353 | 0.7451 | 0.60784 | 0.52941 | 0.29412
FAN | ALL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Office |  | 1 am | 2 am | 3 am | 4 am | 5 am | 6 am | 7 am | 8 am | 9 am | 10 am | 11 am | Noon | 1 pm | 2 pm | 3 pm | 4 pm | 5 pm | 6 pm | 7 pm | 8 pm | 9 pm | 10 pm | 11 pm | 12 pm
Source: AEDG-Warehouse
People | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WEH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lighting | WD | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
| WEH | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
Plug | WD | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
| WEH | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
Infiltration | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Heating* | WD | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 64.94 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 64.94 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
| WEH | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Cooling* | WD | 84.92 | 80.06 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 80.06 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
| WEH | 84.92 | 80.06 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 80.06 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
SWH | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.101 | 0.3985 | 0.5005 | 0.696 | 0.9 | 0.798 | 0.696 | 0.798 | 0.2965 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
| WEH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*Notes: | 1. For climate zones other than 1B, 2B, and 3B occupied cooling thermostat setpoints are maintained continuously (no setback). 2. These schedules reflect optimum start controls. For systems less than 10,000 cfm there is no optimal start and full occupied temperature setpoints begin two hours prior to occupancy instead of being ramped up incrementally beginning two hours prior to occupancy.
Corridor Area |  | 1 am | 2 am | 3 am | 4 am | 5 am | 6 am | 7 am | 8 am | 9 am | 10 am | 11 am | Noon | 1 pm | 2 pm | 3 pm | 4 pm | 5 pm | 6 pm | 7 pm | 8 pm | 9 pm | 10 pm | 11 pm | 12 pm
Lighting | ALL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Elevators |  | 1 am | 2 am | 3 am | 4 am | 5 am | 6 am | 7 am | 8 am | 9 am | 10 am | 11 am | Noon | 1 pm | 2 pm | 3 pm | 4 pm | 5 pm | 6 pm | 7 pm | 8 pm | 9 pm | 10 pm | 11 pm | 12 pm
Elevator Motor | ALL | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
Lighting | ALL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Fan | ALL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Exterior |  | 1 am | 2 am | 3 am | 4 am | 5 am | 6 am | 7 am | 8 am | 9 am | 10 am | 11 am | Noon | 1 pm | 2 pm | 3 pm | 4 pm | 5 pm | 6 pm | 7 pm | 8 pm | 9 pm | 10 pm | 11 pm | 12 pm
Lighting | ALL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1