## Building Description
ASHRAE 90.1 Prototype Building Modeling Specifications
Pacific Northwest National Laboratory, updated on 03-21-2014
| Item | Descriptions |  |  | Data Source
Program
| Vintage | NEW CONSTRUCTION
| Location (Representing 8 Climate Zones) | Zone 1A: Miami (very hot, humid) Zone 1B: Riyadh, Saudi Arabia (very hot, dry) Zone 2A: Houston (hot, humid) Zone 2B: Phoenix (hot, dry) Zone 3A: Memphis (warm, humid) Zone 3B: El Paso (warm, dry) Zone 3C: San Francisco (warm,marine) | Zone 4A: Baltimore (mild, humid) Zone 4B: Albuquerque (mild, dry) Zone 4C: Salem (mild, marine) Zone 5A: Chicago (cold, humid) Zone 5B: Boise (cold, dry) Zone 5C: Vancouver, BC (cold, marine) | Zone 6A: Burlington (cold, humid) Zone 6B: Helena (cold, dry) Zone 7: Duluth (very cold) Zone 8: Fairbanks (subarctic) | Selection of representative climates based on Briggs' paper. See Reference.
| Available fuel types | gas, electricity
| Building Type (Principal Building Function) | OFFICE
| Building Prototype | Medium Office
Form
| Total Floor Area (sq feet) | 53,600 (163.8 ft x 109.2 ft)
Building shape
| Aspect Ratio | 1.5
| Number of Floors | 3
| Window Fraction (Window-to-Wall Ratio) | 33% (Window Dimensions: 163.8 ft x 4.29 ft on the long side of facade 109.2 ft x 4.29 ft on the short side of the façade) |  |  | 2003 CBECS Data and PNNL's CBECS Study 2007.
| Window Locations | even distribution among all four sides
| Shading Geometry | none
| Azimuth | non-directional
| Thermal Zoning | Perimeter zone depth: 15 ft. Each floor has four perimeter zones and one core zone. Percentages of floor area: Perimeter 40%, Core 60%
| Floor to floor height (feet) | 13
| Floor to ceiling height (feet) | 9 (4 ft above-ceiling plenum)
| Glazing sill height (feet) | 3.35 ft (top of the window is 7.64 ft high with 4.29 ft high glass)
Architecture
Exterior walls
| Construction | Steel-Frame Walls (2X4 16IN OC) 0.4 in. Stucco+5/8 in. gypsum board + wall Insulation+5/8 in. |  |  | Construction type: 2003 CBECS Data and PNNL's CBECS Study 2007. Exterior wall layers: default 90.1 layering
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | ASHRAE 90.1 Requirements Nonresidential; Walls, Above-Grade, Steel-Framed |  |  | ASHRAE 90.1
| Dimensions | based on floor area and aspect ratio
| Tilts and orientations | vertical
Roof
| Construction | Built-up Roof: Roof membrane+Roof insulation+metal decking |  |  | Construction type: 2003 CBECS Data and PNNL's CBECS Study 2007. Roof layers: default 90.1 layering
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | ASHRAE 90.1 Requirements Nonresidential; Roofs, Insulation entirely above deck |  |  | ASHRAE 90.1
| Dimensions | based on floor area and aspect ratio
| Tilts and orientations | horizontal
Window
| Dimensions | based on window fraction, location, glazing sill height, floor area and aspect ratio
| Glass-Type and frame | Hypothetical window with weighted U-factor and SHGC
| U-factor (Btu / h * ft2 * °F) | ASHRAE 90.1 Requirements Nonresidential; Vertical Glazing |  |  | ASHRAE 90.1
SHGC (all)
Visible transmittance
| Operable area | 0 |  |  | Ducker Fenestration Market Data provided by the 90.1 envelope subcommittee
Skylight
| Dimensions | Not Modeled
| Glass-Type and frame | NA
U-factor (Btu / h * ft2 * °F)
SHGC (all)
Visible transmittance
Foundation
| Foundation Type | Slab-on-grade floors (unheated)
| Construction | 8" concrete slab poured directly on to the earth
| Thermal properties for ground level floor U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | ASHRAE 90.1 Requirements Nonresidential; Slab-on-Grade Floors, unheated |  |  | ASHRAE 90.1
| Thermal properties for basement walls | NA
| Dimensions | based on floor area and aspect ratio
Interior Partitions
| Construction | 2 x 4 uninsulated stud wall
| Dimensions | based on floor plan and floor-to-floor height
| Internal Mass | 6 inches standard wood (16.6 lb/ft²)
Air Barrier System
| Infiltration | Peak: 0.2016 cfm/sf of above grade exterior wall surface area (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) |  |  | Reference: PNNL-18898: Infiltration Modeling Guidelines for Commercial Building Energy Analysis.
HVAC
System Type
| Heating type | Gas furnace inside the packaged air conditioning unit |  |  | 2003 CBECS Data, PNNL's CBECS Study 2006, and 90.1 Mechanical Subcommittee input.
| Cooling type | Packaged air conditioning unit
| Distribution and terminal units | VAV terminal box with damper and electric reheating coil Zone control type: minimum damper position is calculated using the multiple-zone calculation procedure
HVAC Sizing
| Air Conditioning | autosized to design day
| Heating | autosized to design day
HVAC Efficiency
| Air Conditioning | Various by climate location and design cooling capacity ASHRAE 90.1 Requirements Minimum equipment efficiency for Air Conditioners and Condensing Units |  |  | ASHRAE 90.1
| Heating | Various by climate location and design heating capacity ASHRAE 90.1 Requirements Minimum equipment efficiency for Warm Air Furnaces |  |  | ASHRAE 90.1
HVAC Control
| Thermostat Setpoint | 75°F Cooling/70°F Heating
| Thermostat Setback | 80°F Cooling/60°F Heating
| Supply air temperature | Maximum 104F, Minimum 55F
| Chilled water supply temperatures | NA
| Hot water supply temperatures | NA
| Economizers | Various by climate location and cooling capacity Control type: differential dry bulb |  |  | ASHRAE 90.1
| Ventilation | ASHRAE Ventilation Standard 62.1 See under Outdoor Air. |  |  | ASHRAE Ventilation Standard 62.1
| Demand Control Ventilation | ASHRAE 90.1 Requirements |  |  | ASHRAE 90.1
| Energy Recovery | ASHRAE 90.1 Requirements |  |  | ASHRAE 90.1
Supply Fan
| Fan schedules | See under Schedules
| Supply Fan Total Efficiency (%) | 60% to 62% depending on the fan motor size |  |  | ASHRAE 90.1 requirements for motor efficiency and fan power limitation
| Supply Fan Pressure Drop | Various depending on the fan supply air cfm
Pump
| Pump Type | NA
| Rated Pump Head | NA
| Pump Power | autosized
Cooling Tower
| Cooling Tower Type | NA
| Cooling Tower Efficiency | NA
Service Water Heating
| SWH type | Storage Tank
| Fuel type | Natural Gas
| Thermal efficiency (%) | ASHRAE 90.1 Requirements Water Heating Equipment, Gas storage water heaters, >75,000 Btu/h input |  |  | ASHRAE 90.1
| Tank Volume (gal) | 100 |  |  | Reference: PNNL 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Water temperature setpoint | 140 F
| Water consumption | See under Schedules
Internal Loads & Schedules
Lighting
| Average power density (W/ft2) | ASHRAE 90.1 Lighting Power Densities Using the Building Area Method |  |  | ASHRAE 90.1
| Schedule | See under Schedules
| Daylighting Controls | ASHRAE 90.1 Requirements
| Occupancy Sensors | ASHRAE 90.1 Requirements
Plug load
| Average power density (W/ft2) | See under Zone Summary |  |  | User's Manual for ASHRAE Standard 90.1-2004 (Appendix G)
| Schedule | See under Schedules
Occupancy
| Average people | See under Zone Summary |  |  | User's Manual for ASHRAE Standard 90.1-2004 (Appendix G)
| Schedule | See under Schedules
Misc.
Elevator
| Quantity | 2 |  |  | Reference: DOE Commercial Reference Building Models of the National Building Stock
| Motor type | hydraulic
| Peak Motor Power (W/elevator) | 16055
| Heat Gain to Building | Interior
| Peak Fan/lights Power (W/elevator) | 161.9 |  |  | 90.1 Mechanical Subcommittee, Elevator Working Group
| Motor and fan/lights Schedules | See under Schedules |  |  | DOE Commercial Reference Building TSD and models (V1.3_5.0) and Addendum DF to 90.1-2007
Exterior Lighting
| Peak Power (W) | 14385 |  |  | ASHRAE 90.1
| Schedule | See under Schedules
References
Briggs, R.S., R.G. Lucas, and Z.T. Taylor. 2003. Climate Classification for Building Energy Codes and Standards: Part 2—Zone Definitions, Maps, and Comparisons. ASHRAE Transactions 109(2).
PNNL's CBECS Study. 2007. Analysis of Building Envelope Construction in 2003 CBECS Buildings. Dave Winiarski, Mark Halverson, and Wei Jiang. Pacific Northwest National Laboratory. March 2007.
PNNL's CBECS Study. 2006. Review of Pre- and Post-1980 Buildings in CBECS – HVAC Equipment. Dave Winiarski, Wei Jiang and Mark Halverson. Pacific Northwest National Laboratory. December 2006.
Gowri K, DW Winiarski, and RE Jarnagin. 2009. Infiltration modeling guidelines for commercial building energy analysis . PNNL-18898, Pacific Northwest National Laboratory, Richland, WA. http://www.pnl.gov/main/publications/external/technical_reports/PNNL-18898.pdf
PNNL. 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models. Pacific Northwest National Laboratory, Richland, Washington. Available at https://www.energycodes.gov/development/commercial/90.1_models.

## Zone Summary
Zone Summary
(90.1-2004 baseline requirements for LPD)
Zone | Area [ft²] | Conditioned [Y/N] | Volume [ft³] | Multipliers | Gross Wall Area [ft²] | Window Glass Area [ft²] | Lighting [W/ft²] | People [ft²/person] | Number of People | Plug and Process [W/ft²]
CORE_BOTTOM | 10587.8081 | Yes | 95294.7728 | 1 | 0 | 0 | 1 | 200 | 52.939 | 0.75
TOPFLOOR_PLENUM | 17877.7585 | Yes | 71514.5232 | 1 | 2183.5726 | 0 | 0 | - | 0 | 0.75
MIDFLOOR_PLENUM | 17877.7585 | Yes | 71514.5232 | 1 | 2183.5726 | 0 | 0 | - | 0 | 0.75
FIRSTFLOOR_PLENUM | 17877.7585 | Yes | 71514.5232 | 1 | 2183.5726 | 0 | 0 | - | 0 | 0.75
CORE_MID | 10587.8081 | Yes | 95294.7728 | 1 | 0 | 0 | 1 | 200 | 52.939 | 0.75
CORE_TOP | 10587.8081 | Yes | 95294.7728 | 1 | 0 | 0 | 1 | 200 | 52.939 | 0.75
PERIMETER_TOP_ZN_3 | 2232.0151 | Yes | 20088.9564 | 1 | 1473.9438 | 702.7392 | 1 | 200 | 11.1601 | 0.75
PERIMETER_TOP_ZN_2 | 1413.0139 | Yes | 12718.0256 | 1 | 982.6292 | 468.4928 | 1 | 200 | 7.0651 | 0.75
PERIMETER_TOP_ZN_1 | 2232.0151 | Yes | 20088.9564 | 1 | 1473.9438 | 702.7392 | 1 | 200 | 11.1601 | 0.75
PERIMETER_TOP_ZN_4 | 1412.9062 | Yes | 12716.966 | 1 | 982.6292 | 468.4928 | 1 | 200 | 7.0645 | 0.75
PERIMETER_BOT_ZN_3 | 2232.0151 | Yes | 20088.9564 | 1 | 1473.9438 | 702.7392 | 1 | 200 | 11.1601 | 0.75
PERIMETER_BOT_ZN_2 | 1413.0139 | Yes | 12718.0256 | 1 | 982.6292 | 468.4928 | 1 | 200 | 7.0651 | 0.75
PERIMETER_BOT_ZN_1 | 2232.0151 | Yes | 20088.9564 | 1 | 1473.9438 | 702.7392 | 1 | 200 | 11.1601 | 0.75
PERIMETER_BOT_ZN_4 | 1412.9062 | Yes | 12716.966 | 1 | 982.6292 | 468.4928 | 1 | 200 | 7.0645 | 0.75
PERIMETER_MID_ZN_3 | 2232.0151 | Yes | 20088.9564 | 1 | 1473.9438 | 702.7392 | 1 | 200 | 11.1601 | 0.75
PERIMETER_MID_ZN_2 | 1413.0139 | Yes | 12718.0256 | 1 | 982.6292 | 468.4928 | 1 | 200 | 7.0651 | 0.75
PERIMETER_MID_ZN_1 | 2232.0151 | Yes | 20088.9564 | 1 | 1473.9438 | 702.7392 | 1 | 200 | 11.1601 | 0.75
PERIMETER_MID_ZN_4 | 1412.9062 | Yes | 12716.966 | 1 | 982.6292 | 468.4928 | 1 | 200 | 7.0645 | 0.75
TOTAL1 | 53633.2753 |  | 697266.6012 |  | 21290.1558 | 7027.392 |  |  | 268.1664
AREA WEIGHTED AVERAGE | [6 empty] | 1 | 200
1. Only volume, and gross wall area include unconditioned space.

## Outdoor Air
Minimum Outdoor Ventilation Air Requirements
|  |  |  | Total Occupants | Total OSA Ventilation (cfm/zone) |  |  | Total OSA Ventilation (cfm/ft2)
Zone | Area (ft2) | Multipliers | Assumed Space Type | 62.1-2004 | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007) | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007)
CORE_BOTTOM | 10587.8081 | 1 | Office space | 52.939 | 1058.7808 | 899.9637 | 899.9637 | 0.1 | 0.085 | 0.085
CORE_MID | 10587.8081 | 1 | Office space | 52.939 | 1058.7808 | 899.9637 | 899.9637 | 0.1 | 0.085 | 0.085
CORE_TOP | 10587.8081 | 1 | Office space | 52.939 | 1058.7808 | 899.9637 | 899.9637 | 0.1 | 0.085 | 0.085
PERIMETER_TOP_ZN_3 | 2232.0151 | 1 | Office space | 11.1601 | 223.2015 | 189.7213 | 189.7213 | 0.1 | 0.085 | 0.085
PERIMETER_TOP_ZN_2 | 1412.9062 | 1 | Office space | 7.0645 | 141.2906 | 120.097 | 120.097 | 0.1 | 0.085 | 0.085
PERIMETER_TOP_ZN_1 | 2232.0151 | 1 | Office space | 11.1601 | 223.2015 | 189.7213 | 189.7213 | 0.1 | 0.085 | 0.085
PERIMETER_TOP_ZN_4 | 1412.9062 | 1 | Office space | 7.0645 | 141.2906 | 120.097 | 120.097 | 0.1 | 0.085 | 0.085
PERIMETER_BOT_ZN_3 | 2232.0151 | 1 | Office space | 11.1601 | 223.2015 | 189.7213 | 189.7213 | 0.1 | 0.085 | 0.085
PERIMETER_BOT_ZN_2 | 1412.9062 | 1 | Office space | 7.0645 | 141.2906 | 120.097 | 120.097 | 0.1 | 0.085 | 0.085
PERIMETER_BOT_ZN_1 | 2232.0151 | 1 | Office space | 11.1601 | 223.2015 | 189.7213 | 189.7213 | 0.1 | 0.085 | 0.085
PERIMETER_BOT_ZN_4 | 1412.9062 | 1 | Office space | 7.0645 | 141.2906 | 120.097 | 120.097 | 0.1 | 0.085 | 0.085
PERIMETER_MID_ZN_3 | 2232.0151 | 1 | Office space | 11.1601 | 223.2015 | 189.7213 | 189.7213 | 0.1 | 0.085 | 0.085
PERIMETER_MID_ZN_2 | 1412.9062 | 1 | Office space | 7.0645 | 141.2906 | 120.097 | 120.097 | 0.1 | 0.085 | 0.085
PERIMETER_MID_ZN_1 | 2232.0151 | 1 | Office space | 11.1601 | 223.2015 | 189.7213 | 189.7213 | 0.1 | 0.085 | 0.085
PERIMETER_MID_ZN_4 | 1412.9062 | 1 | Office space | 7.0645 | 141.2906 | 120.097 | 120.097 | 0.1 | 0.085 | 0.085
TOTAL | 53632.9524 |  |  | 268.1648 | 5363.2952 | 4558.801 | 4558.801 | 0.1 | 0.085 | 0.085
Residential single bedroom apartment
Corridors (public spaces)
Office space

## Schedules
Schedule | Type | Through | Day of Week | 1 am | 2 am | 3 am | 4 am | 5 am | 6 am | 7 am | 8 am | 9 am | 10 am | 11 am | Noon | 1 pm | 2 pm | 3 pm | 4 pm | 5 pm | 6 pm | 7 pm | 8 pm | 9 pm | 10 pm | 11 pm | 12 pm
Internal Loads Schedules
BLDG_LIGHT_SCH | Fraction | Through 12/31 | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_EQUIP_SCH | Fraction | Through 12/31 | Weekday | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  |  | Saturday | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH | Fraction | Through 12/31 | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_ELEVATORS | Fraction | Through 12/31 | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0
|  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exterior Lighting Schedule
BLDG_EXTERIOR_LIGHT | Fraction | Through 12/31 | All Days | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
(AstronomicalClock control)
Service Water Heater Load Schedule
BLDG_SWH_SCH | Fraction | Through 12/31 | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
|  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0 | 0 | 0 | 0
Infiltration Schedule
INFIL_SCH_PNNL | Fraction | Through 12/31 | Weekday, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
|  |  | Saturday, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HVAC Schedules
HVACOperationSchd | On/off | Through 12/31 | Weekday, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
(Fan Schedule) |  |  | Saturday, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HTGSETP_SCH | Temperature | Through 12/31 | Weekday | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
|  |  | Saturday | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
|  |  | WinterDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
CLGSETP_SCH | Temperature | Through 12/31 | Weekday | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
|  |  | Saturday | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
|  |  | Sun, Hol, Other | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
| (°C) |  | SummerDesign | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
HTGSETP_SCH* | Temperature | Through 12/31 | Weekday | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 64.04 | 68 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 60.08 | 60.08
| (°F) |  | Saturday | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 64.04 | 68 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
|  |  | Sun, Hol, Other | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
|  |  | WinterDesign | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 63.68 | 67.28 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 60.08 | 60.08
CLGSETP_SCH* | Temperature | Through 12/31 | Weekday | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 78.08 | 77 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 80.06 | 80.06
| (°F) |  | Saturday | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 78.26 | 77 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 80.06 | 80.06
|  |  | Sun, Hol, Other | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06
|  |  | SummerDesign | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 78.26 | 77 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 80.06 | 80.06
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Sched | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
*Notes: | 1. For climate zones other than 1B, 2B, and 3B occupied cooling thermostat setpoints are maintained continuously (no setback). 2. These schedules reflect optimum start controls. For systems less than 10,000 cfm there is no optimal start and full occupied temperature setpoints begin two hours prior to occupancy instead of being ramped up incrementally beginning two hours prior to occupancy.