## Building Description
ASHRAE 90.1 Prototype Building Modeling Specifications
Pacific Northwest National Laboratory, updated on 03-21-2014
| Item | Descriptions |  |  | Data Source
Program
| Vintage | NEW CONSTRUCTION
| Location (Representing 8 Climate Zones) | Zone 1A: Miami (very hot, humid) Zone 1B: Riyadh, Saudi Arabia (very hot, dry) Zone 2A: Houston (hot, humid) Zone 2B: Phoenix (hot, dry) Zone 3A: Memphis (warm, humid) Zone 3B: El Paso (warm, dry) Zone 3C: San Francisco (warm,marine) | Zone 4A: Baltimore (mild, humid) Zone 4B: Albuquerque (mild, dry) Zone 4C: Salem (mild, marine) Zone 5A: Chicago (cold, humid) Zone 5B: Boise (cold, dry) Zone 5C: Vancouver, BC (cold, marine) | Zone 6A: Burlington (cold, humid) Zone 6B: Helena (cold, dry) Zone 7: Duluth (very cold) Zone 8: Fairbanks (subarctic) | Selection of representative climates based on Briggs' paper. See Reference.
| Available fuel types | gas, electricity
| Building Type (Principal Building Function) | FOOD SERVICE
| Building Prototype | Fast Food
Form
| Total Floor Area (sq feet) | 2500 (50 ft x 50 ft)
Building shape
| Aspect Ratio | 1
| Number of Floors | 1
| Window Fraction (Window-to-Wall Ratio) | South: 28% East: 14% North: 0% West: 14% Total: 14%
| Window Locations | East (23.3 ft x 3 ft), south (46.7 ft x 3 ft), and west (23.3 ft x 3 ft) sides of dining zone façade
| Shading Geometry | none
| Azimuth | non-directional
| Thermal Zoning | Kitchen, Dining, and Unconditioned Attic (See ZoneSummary tab)
| Floor to floor height (feet) | NA
| Floor to ceiling height (feet) | 10
| Glazing sill height (feet) | 3.5 (top of the window is 6.5 ft high with 3 ft high glass)
Architecture
Exterior walls
| Construction | Wood-framed wall: 1 in. stucco + 0.625 in. gypsum board + wall insulation + 0.625 in. gypsum board |  |  | Construction type: 2003 CBECS Data and PNNL's CBECS Study 2007. Exterior wall layers: default 90.1 layering
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | ASHRAE 90.1 Requirements Nonresidential; Walls, Above-Grade, Wood-framed |  |  | ASHRAE 90.1
| Dimensions | based on floor area and aspect ratio
| Tilts and orientations | Vertical
Roof
| Construction | Unconditioned attic roof modeled with asphalt shingles and 0.625 in. gypsum board (no insulation). Ceiling between attic and conditioned zones modeled with wood-joist attic roof consisting of the following layers: insulation and 0.625 in. gypsum board |  |  | Construction type: 2003 CBECS Data and PNNL's CBECS Study 2007. Roof layers: default 90.1 layering
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Attic Roof (all zones): 0.071 - No Insulation Ceiling: ASHRAE 90.1 Requirements Nonresidential; Roofs, Attic and other |  |  | ASHRAE 90.1
| Dimensions | based on floor area and aspect ratio
| Tilts and orientations | Insulated Ceiling - horizontal Attic Roof East & West - 45 deg. North & South - 18.44 deg.
Window
| Dimensions | based on window fraction, location, glazing sill height, floor area and aspect ratio
| Glass-Type and frame | Hypothetical window with weighted U-factor and SHGC
| U-factor (Btu / h * ft2 * °F) | ASHRAE 90.1 Requirements Nonresidential; Vertical Glazing |  |  | ASHRAE 90.1
SHGC (all)
| Visible transmittance |  |  |  | Ducker Fenestration Market Data provided by the 90.1 envelope subcommittee
| Operable area | 2% of total WWR |  |  | Ducker Fenestration Market Data provided by the envelope subcommittee
Skylight
| Dimensions | Not Modeled
| Glass-Type and frame | NA
U-factor (Btu / h * ft2 * °F)
SHGC
Visible transmittance
Foundation
| Foundation Type | Slab-on-grade floors (unheated)
| Construction | 6" concrete slab poured directly on to the earth
| Thermal properties for ground level floor U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | ASHRAE 90.1 Requirements Nonresidential; Slab-on-Grade Floors, unheated |  |  | ASHRAE 90.1
| Thermal properties for basement walls | NA
| Dimensions | based on floor area and aspect ratio
Interior Partitions
| Construction | 0.5 in gypsum board + 0.5 in gypsum board
| Dimensions | based on floor plan and floor-to-floor height
| Internal Mass | 6 inches standard wood (16.6 lb/ft²)
Air Barrier System
| Infiltration | Peak: 0.2016 cfm/sf of above grade exterior wall surface area (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) |  |  | Reference: PNNL-18898: Infiltration Modeling Guidelines for Commercial Building Energy Analysis.
HVAC
System Type
| Heating type | Gas furnace inside the packaged air conditioning unit |  |  | 2003 CBECS Data, PNNL's CBECS Study 2006, and 90.1 Mechanical Subcommittee input.
| Cooling type | Packaged air conditioning unit
| Distribution and terminal units | Single zone, constant air volume air distribution
HVAC Sizing
| Air Conditioning | autosized to design day
| Heating | autosized to design day
HVAC Efficiency
| Air Conditioning | Various by climate location and design cooling capacity ASHRAE 90.1 Requirements Minimum equipment efficiency for Air Conditioners and Condensing Units |  |  | ASHRAE 90.1
| Heating | Various by climate location and design heating capacity ASHRAE 90.1 Requirements Minimum equipment efficiency for Warm Air Furnaces |  |  | ASHRAE 90.1
HVAC Control
| Thermostat Setpoint | Dining - 75°F Cooling/70°F Heating Kitchen - 79°F Cooling/66°F Heating
| Thermostat Setback | Dining - 86°F Cooling/60°F Heating Kitchen - 86°F Cooling/60°F Heating
| Supply air temperature | Maximum 104°F, Minimum 55°F
| Chilled water supply temperatures | NA
| Hot water supply temperatures | NA
| Economizers | Various by climate location and cooling capacity Control type: differential dry bulb |  |  | ASHRAE 90.1
| Ventilation | ASHRAE Ventilation Standard 62.1 and additional OSA to replace the 3,300 cfm kitchen exhaust flow See under Outdoor Air. |  |  | ASHRAE Ventilation Standard 62.1
| Demand Control Ventilation | No |  |  | ASHRAE 90.1
| Energy Recovery | No |  |  | ASHRAE 90.1
Supply Fan
| Fan schedules | See under Schedules
| Supply Fan Total Efficiency (%) | Various depending on the fan motor size |  |  | ASHRAE 90.1 requirements for motor efficiency and fan power limitation
| Supply Fan Pressure Drop | Various depending on the fan supply air cfm
Pump
| Pump Type | N/A
| Rated Pump Head | No
| Pump Power | N/A
Cooling Tower
| Cooling Tower Type | NA
| Cooling Tower Power | NA
Service Water Heating
| SWH type | Storage Tank
| Fuel type | Natural Gas
| Thermal efficiency (%) | ASHRAE 90.1 Requirements |  |  | ASHRAE 90.1
| Tank Volume (gal) | 100 |  |  | Reference: PNNL 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Water temperature setpoint | 140 F
| Water consumption | BLDG_SWH_SCH See under Schedules
Internal Loads & Schedules
Lighting
| Average power density (W/ft2) | ASHRAE 90.1 Lighting Power Densities Using the Building Area Method
| Schedule | See under Schedules
| Daylighting Controls | ASHRAE 90.1 Requirements
| Occupancy Sensors | ASHRAE 90.1 Requirements
Plug load
| Average power density (W/ft2) | See under Zone Summary
| Schedule | See under Schedules
Occupancy
| Average people | See under Zone Summary
| Schedule | See under Schedules
Misc.
Elevator
| Peak Power | NA
| Schedule | NA
Exterior Lighting
| Peak Power | 1743 watts |  |  | ASHRAE 90.1
| Schedule | Astronomical Clock
References
Briggs, R.S., R.G. Lucas, and Z.T. Taylor. 2003. Climate Classification for Building Energy Codes and Standards: Part 2—Zone Definitions, Maps, and Comparisons. ASHRAE Transactions 109(2).
PNNL's CBECS Study. 2007. Analysis of Building Envelope Construction in 2003 CBECS Buildings. Dave Winiarski, Mark Halverson, and Wei Jiang. Pacific Northwest National Laboratory. March 2007.
PNNL's CBECS Study. 2006. Review of Pre- and Post-1980 Buildings in CBECS – HVAC Equipment. Dave Winiarski, Wei Jiang and Mark Halverson. Pacific Northwest National Laboratory. December 2006.
Gowri K, DW Winiarski, and RE Jarnagin. 2009. Infiltration modeling guidelines for commercial building energy analysis . PNNL-18898, Pacific Northwest National Laboratory, Richland, WA. http://www.pnl.gov/main/publications/external/technical_reports/PNNL-18898.pdf
PNNL. 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models. Pacific Northwest National Laboratory, Richland, Washington. Available at https://www.energycodes.gov/development/commercial/90.1_models.
Kitchen
Dining

## Zone Summary
Zone Summary
(90.1-2004 baseline requirements for LPD)
Zone | Area [ft²] | Conditioned [Y/N] | Volume [ft³] | Multipliers | Gross Wall Area [ft²] | Window Glass Area [ft²] | Lighting [W/ft²] | People [ft²/person] | Number of People | Plug and Process, Electricity [W/ft²] | Plug and Process, Gas [W/ft²]
DINING | 1250.4434 | Yes | 12507.7498 | 1 | 1000.3978 | 280.0769 | 2.1 | 14.316 | 87.3459 | 10.85 | 0
KITCHEN | 1250.4434 | Yes | 12507.7498 | 1 | 1000.3978 | 0 | 1.2 | 199.3476 | 6.2727 | 25.31 | 73.52
ATTIC | 2500.8868 | No | 9264.4505 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL1 | 2500.8868 |  | 34280.3033 |  | 2000.9032 | 280.0769 |  |  | 93.6185
AREA WEIGHTED AVERAGE | [6 empty] | 1.65 | 106.8318 |  | 18.08 | 36.76
1. Only volume, and gross wall area include unconditioned space.

## Outdoor Air
Minimum Outdoor Ventilation Air Requirements
|  |  |  | Occupant Density (Sqft/Person) (Note 1) |  |  |  | Total Occupants | Total OSA Ventilation (cfm/zone) (Note 2) |  |  | Total OSA Ventilation (cfm/ft2) (Note 2)
Zone | Area (sqft) | Multiplier | Assumed Space Type | 90.1-1989 | 62-1999 | 62.1-2004 | 62.1-2007 | 62.1-2004 | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007) | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007)
DINING | 1250.4434 | 1 | Restaurant dining rooms | 100 | 14.2857 | 14.2857 | 14.2857 | 87.531 | 1750.6208 | 881.5626 | 881.5626 | 1.4 | 0.705 | 0.705
KITCHEN | 1250.4434 | 1 | Kitchen | 100 | 50 | NA | NA | 6 | 90 | 875.3104 | 875.3104 | 0.071974 | 0.7 | 0.7
TOTAL2 | 2500.8868 | [6 empty] | 93.531 | 1840.6208 | 1756.873 | 1756.873 | 0.73599 | 0.7025 | 0.7025
1. Kitchen occupancy not included in ASHRAE 62.1-2004, therefore the value is from the DOE's benchmark model V1.0_3.0
2. In order to provide sufficient OSA to replace exhaust flow through kitchen hoods (3,300 cfm), modeled OSA to kitchen is different from OSA determined based on ASHRAE 62.1. It takes into account the available OSA in dining as transfer air.

## Schedules
Schedule | Type | Through | Day of Week | 1 am | 2 am | 3 am | 4 am | 5 am | 6 am | 7 am | 8 am | 9 am | 10 am | 11 am | Noon | 1 pm | 2 pm | 3 pm | 4 pm | 5 pm | 6 pm | 7 pm | 8 pm | 9 pm | 10 pm | 11 pm | 12 pm
Internal Loads Schedules
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
|  |  | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
|  |  | Sun, Hol, Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
|  |  | Sat | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
|  |  | Sun, Hol, Other | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
|  |  | SummerDesign | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FF_GAS_EQUIP_SCH | Fraction | Through 12/31 | WD, Sat | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
|  |  | Sun, Hol, Other | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
|  |  | SummerDesign | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
|  |  | Sat | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
|  |  | Sun, Hol, Other | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exterior Loads Schedules
BLDG_EXTERIOR_LIGHT | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
(AstronomicalClock control) |  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Service Water Heater Load Schedule
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.33 | 0.13 | 0.1 | 0.72 | 0.31 | 0.98 | 0.92 | 0.22 | 0.31 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0.15
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.33 | 0.13 | 0.1 | 0.72 | 0.31 | 0.98 | 0.92 | 0.22 | 0.31 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0.15
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.33 | 0.13 | 0.1 | 0.72 | 0.31 | 0.98 | 0.92 | 0.22 | 0.31 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0
Infiltration Schedule
INFIL_SCH_PNNL | fraction | Through 12/31 | WD, SummerDesign | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  | Sat, WinterDesign | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  | Sun, Hol, Other | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HVAC Schedules
HVACOperationSchd | on/off | Through 12/31 | WD, SummerDesign | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
(FAN_SCH) |  |  | Sat, WinterDesign | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sun, Hol, Other | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HTGSETP_SCH | Temperature | Through 12/31 | WD | 13 | 13 | 13 | 13 | 13 | 13 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 13 | 13 | 13 | 13 | 13
| (°C) |  | SummerDesign | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
|  |  | Sat | 13 | 13 | 13 | 13 | 13 | 13 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
|  |  | Sun, Hol, Other | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
CLGSETP_SCH | Temperature | Through 12/31 | WD | 33 | 33 | 33 | 33 | 33 | 33 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 33 | 33
| (°C) |  | SummerDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  |  | Sat | 33 | 33 | 33 | 33 | 33 | 33 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 33 | 33 | 33 | 33 | 33 | 33
|  |  | WinterDesign | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33
|  |  | Sun, Hol, Other | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
| (°C) | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
|  | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
HTGSETP_DINING_SCH | Temperature | Through 12/31 | WD, Winter Design | 60 | 60 | 60 | 60 | 60 | 65 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
| (°F) |  | SummerDesign | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  | Sat, Sun, Hol, Other | 60 | 60 | 60 | 60 | 60 | 65 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
HTGSETP_KITCHEN_SCH | Temperature | Through 12/31 | WD, Winter Design | 60 | 60 | 60 | 60 | 60 | 63 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
| (°F) |  | SummerDesign | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  | Sat, Sun, Hol, Other | 60 | 60 | 60 | 60 | 60 | 63 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
CLGSETP_DINING_SCH | Temperature | Through 12/31 | WD, SummerDesign | 86 | 86 | 86 | 86 | 86 | 80 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
| (°F) |  | WinterDesign | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86
|  |  | Sat, Sun, Hol, Other | 86 | 86 | 86 | 86 | 86 | 80 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
CLGSETP_KITCHEN_SCH | Temperature | Through 12/31 | WD, SummerDesign | 86 | 86 | 86 | 86 | 86 | 83 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
| (°F) |  | WinterDesign | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86
|  |  | Sat, Sun, Hol, Other | 86 | 86 | 86 | 86 | 86 | 83 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
HTGSETP_DINING_SCH | Temperature | Through 12/31 | WD, Winter Design | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 18.3333 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111
| (°C) |  | SummerDesign | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556
|  |  | Sat, Sun, Hol, Other | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 18.3333 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111 | 21.1111
HTGSETP_KITCHEN_SCH | Temperature | Through 12/31 | WD, Winter Design | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 17.2222 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889
| (°C) |  | SummerDesign | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556
|  |  | Sat, Sun, Hol, Other | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 15.5556 | 17.2222 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889 | 18.8889
CLGSETP_DINING_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 26.6667 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889
| (°C) |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  |  | Sat, Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 26.6667 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889 | 23.8889
CLGSETP_KITCHEN_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 28.3333 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111
| (°C) |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  |  | Sat, Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 28.3333 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111 | 26.1111
MinOA_FFKitch_Sched (for kichen) | fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
MinOA_Sched (for dining) | fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1

## SchedulePlots
Restaurant FastFood: Weekday Schedules