## Building Description
ASHRAE 90.1 Prototype Building Modeling Specifications
Pacific Northwest National Laboratory, updated on 03-21-2014
| Item | Descriptions |  |  | Data Source
Program
| Vintage | NEW CONSTRUCTION
| Location (Representing 8 Climate Zones) | Zone 1A: Miami (very hot, humid) Zone 1B: Riyadh, Saudi Arabia (very hot, dry) Zone 2A: Houston (hot, humid) Zone 2B: Phoenix (hot, dry) Zone 3A: Memphis (warm, humid) Zone 3B: El Paso (warm, dry) Zone 3C: San Francisco (warm,marine) | Zone 4A: Baltimore (mild, humid) Zone 4B: Albuquerque (mild, dry) Zone 4C: Salem (mild, marine) Zone 5A: Chicago (cold, humid) Zone 5B: Boise (cold, dry) Zone 5C: Vancouver, BC (cold, marine) | Zone 6A: Burlington (cold, humid) Zone 6B: Helena (cold, dry) Zone 7: Duluth (very cold) Zone 8: Fairbanks (subarctic) | Selection of representative climates based on Briggs' paper
| Available fuel types | gas, electricity
| Building Type (Principal Building Function) | EDUCATION
| Building Prototype | Primary School
Form
| Total Floor Area (sq feet) | 73, 960 (340 ft x 270 ft)
Building shape
| Aspect Ratio | 1.3
| Number of Floors | 1
| Window Fraction (Window-to-Wall Ratio) | 35% for all facades Ribbon window across all facades
| Window Locations | Continuous Band
| Shading Geometry | none
| Azimuth | non-directional
| Thermal Zoning | Classrooms zoned by exposure. Corner classrooms separated out from single exposure classrooms. Double loaded corridors zoned separately. Administrative area, Gymnasium , mechanical, media center, lobby, kitchen, and cafeteria are single zones. See Zone Summary.
| Floor to floor height (feet) | 13
| Floor to ceiling height (feet) | 13
| Glazing sill height (feet) | 3.6 (top of the window is 8.1 ft high with 4.5 ft high glass)
Architecture
Exterior walls
| Construction | Steel-framed Walls (2x4, 16" OC) 0.75" stucco + 0.625" gypsum board + Cavity insulation + 0.625" gypsum board |  |  | Construction type: 2003 CBECS Data and PNNL's CBECS Study 2007. Exterior wall layers: default 90.1 layering
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | ASHRAE 90.1 Requirements Nonresidential; Walls, Above-Grade, Steel-Framed |  |  | ASHRAE 90.1
| Dimensions | based on floor area and aspect ratio
| Tilts and orientations | vertical
Roof
| Construction | Built-up Roof Roof membrane + Roof insulation + Metal decking |  |  | Construction type: 2003 CBECS Data and PNNL's CBECS Study 2007. Roof layers: default 90.1 layering
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | ASHRAE 90.1 Requirements Nonresidential; Roofs, Insulation entirely above deck |  |  | ASHRAE 90.1
| Area (ft2) | 73960
| Tilts and orientations | horizontal
Window
| Dimensions | based on window fraction, location, glazing sill height, floor area and aspect ratio
| Glass-Type and frame | Hypothetical window with weighted U-factor and SHGC
| U-factor (Btu / h * ft2 * °F) | ASHRAE 90.1 Requirements Nonresidential; Vertical Glazing, 30.1-40% |  |  | ASHRAE 90.1
SHGC (all)
Visible transmittance
| Operable area | 35% |  |  | PNNL 's Glazing Market Data for ASHRAE spreadsheet
Skylight
| Dimensions | Gymnasium/Multipurpose Room (4 ft x 4 ft) x 9 skylights = 144 ft² total Skylight Area 3.75% of gym roof area |  |  | AEDG K-12 Guide
| Glass-Type and frame | Hypothetical glass and frame meeting ASHRAE 90.1 Requirements below
| U-factor (Btu / h * ft2 * °F) | ASHRAE 90.1 Requirements Nonresidential; Skylight with curb, Glass, 2.1-5% |  |  | ASHRAE 90.1
SHGC
Visible transmittance
Foundation
| Foundation Type | Slab-on-grade floors (unheated)
| Construction | 6" concrete slab poured directly on to the earth + carpet
| Thermal properties for ground level floor F-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | ASHRAE 90.1 Requirements Nonresidential; Slab-on-Grade Floors, unheated |  |  | ASHRAE 90.1
| Thermal properties for basement walls | NA
| Dimensions | based on floor area and aspect ratio
Interior Partitions
| Construction | 2 x 4 uninsulated stud wall
| Dimensions | based on floor plan and floor-to-floor height
| Internal Mass | 6 inches standard wood (16.6 lb/ft²)
Air Barrier System
| Infiltration | Peak: 0.2016 cfm/ft² of above grade exterior wall surface area (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) |  |  | Reference: PNNL-18898: Infiltration Modeling Guidelines for Commercial Building Energy Analysis.
HVAC
System Type
| Heating type | 1. Gas furnace inside packaged air conditioning unit 2. Hot water from a gas boiler for heating |  |  | 2003 CBECS Data, PNNL's CBECS Study 2006, and 90.1 Mechanical Subcommittee input.
| Cooling type | Packaged air conditioning unit
| Distribution and terminal units | 1. CAV systems: direct air from the packaged air conditioning unit 2. VAV systems: VAV terminal box with damper and hot water reheating coil Zone Control Type: minimum supply air at 30% of the zone design peak supply air
HVAC Sizing
| Air Conditioning | autosized to design day
| Heating | autosized to design day
HVAC Efficiency
| Air Conditioning | Varies by climate location and design cooling capacity ASHRAE 90.1 Requirements Minimum equipment efficiency for Air Conditioners and Condensing Units |  |  | ASHRAE 90.1
| Heating | Varies by climate location and design heating capacity ASHRAE 90.1 Requirements Minimum equipment efficiency for Warm Air Furnaces Minimum equipment efficiency for Gas and Oil-fired Boilers |  |  | ASHRAE 90.1
HVAC Control
| Thermostat Setpoint | 75°F Cooling/70°F Heating
| Thermostat Setback | 80°F Cooling/60°F Heating
| Supply air temperature | Minimum 50 °F and maximum 122 °F
| Chilled water supply temperatures | NA
| Hot water supply temperatures | 180 °F
| Economizers | Varies by climate location and cooling capacity Control type: differential dry bulb |  |  | ASHRAE 90.1
| Outdoor Air Ventilation | ASHRAE Ventilation Standard 62.1 See under Outdoor Air. |  |  | ASHRAE Ventilation Standard 62.1
| Demand Control Ventilation | ASHRAE 90.1 Requirements |  |  | ASHRAE 90.1
| Energy Recovery | ASHRAE 90.1 Requirements |  |  | ASHRAE 90.1
Supply Fan
| Fan schedules | See under Schedules
| Supply Fan Mechanical Efficiency (%) | Varies depending on the fan motor size and type of fan |  |  | ASHRAE 90.1 requirements for motor efficiency and fan power limitation
| Supply Fan Pressure Drop | Various depending on the fan supply air cfm
Pump
| Pump Type | Variable speed
| Rated Pump Head | 60 ft
| Pump Power | autosized
Cooling Tower
| Cooling Tower Type | NA
| Cooling Tower Power | NA
Service Water Heating
| SWH type | Storage Tank
| Fuel type | Natural Gas (main); Electric (dishwasher booster) |  |  | Reference: PNNL 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Thermal efficiency (%) | ASHRAE 90.1 Requirements |  |  | ASHRAE 90.1
| Tank Volume (gal) | 200 (main); 6 (dishwasher booster) |  |  | Reference: PNNL 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Water temperature setpoint | 140 F (main); 180 F (dishwasher booster)
| Water consumption (peak gpm) | See under Schedules
Internal Loads & Schedules
Lighting
| Lighting power density (W/ft2) | ASHRAE 90.1 Lighting Power Densities Using the Space-By-Space Method See under Zone Summary |  |  | ASHRAE 90.1
| Schedule | See under Schedules
| Daylighting Controls | ASHRAE 90.1 Requirements
| Occupancy Sensors | ASHRAE 90.1 Requirements
Plug load
| Average power density (W/ft2) | See under Zone Summary |  |  | User's Manual for ASHRAE Standard 90.1-2004 (Appendix G)
| Schedule | See under Schedules
Refrigeration
| Equipment | Walk-in freezer and display case both with air-cooled local condensers
Occupancy
| Average people | See under Zone Summary
| Schedule | See under Schedules
Misc.
Elevator
| Peak Power | Not modeled.
| Schedule | Not modeled.
Exterior Lighting
| Peak Power (W) | ASHRAE 90.1 Lighting Power Densities For Building Exteriors |  |  | ASHRAE 90.1
| Schedule | See under Schedules
References
1 | Briggs, R.S., R.G. Lucas, and Z.T. Taylor. 2003. Climate Classification for Building Energy Codes and Standards: Part 2—Zone Definitions, Maps, and Comparisons. ASHRAE Transactions 109(2).
2 | PNNL's CBECS Study. 2007. Analysis of Building Envelope Construction in 2003 CBECS Buildings. Dave Winiarski, Mark Halverson, and Wei Jiang. Pacific Northwest National Laboratory. March 2007.
3 | PNNL's CBECS Study. 2006. Review of Pre- and Post-1980 Buildings in CBECS – HVAC Equipment. Dave Winiarski, Wei Jiang and Mark Halverson. Pacific Northwest National Laboratory. December 2006.
“Study of the U.S. Market For Windows, Doors, and Skylights”, American Architectural Manufacturers Association, Window & Door Manufacturers Association, 2006.
PNNL. 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models. Pacific Northwest National Laboratory, Richland, Washington. Available at https://www.energycodes.gov/development/commercial/90.1_models.

## Zone Summary
Zone Summary
(90.1-2004 baseline requirements for LPD)
Zone Name | Area [ft²] | Conditioned [Y/N] | Volume [ft³] | Multipliers | Gross Wall Area [ft²] | Window Glass Area [ft²] | Lighting [W/ft²] | People [ft²/person] | Number of People | Plug and Process [W/ft²]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 1065.7308 | Yes | 13986.6566 | 1 | 861.1966 | 301.4188 | 1.3999 | 40.0456 | 26.6129 | 1.3934
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 5134.8849 | Yes | 67390.2547 | 1 | 2282.1711 | 798.7599 | 1.3999 | 40.0456 | 128.2258 | 1.3934
CORRIDOR_POD_1_ZN_1_FLR_1 | 2066.8719 | Yes | 27125.6371 | 1 | 129.1795 | 45.2128 | 0.49996 | 0 | - | 0.37158
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 1065.7308 | Yes | 13986.6566 | 1 | 861.1966 | 301.4188 | 1.3999 | 40.0456 | 26.6129 | 1.3934
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 5134.8849 | Yes | 67390.2547 | 1 | 2282.1711 | 798.7599 | 1.3999 | 40.0456 | 128.2258 | 1.3934
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 1065.7308 | Yes | 13986.6566 | 1 | 861.1966 | 301.4188 | 1.3999 | 40.0456 | 26.6129 | 1.3934
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 5134.8849 | Yes | 67390.2547 | 1 | 2282.1711 | 798.7599 | 1.3999 | 40.0456 | 128.2258 | 1.3934
CORRIDOR_POD_2_ZN_1_FLR_1 | 2066.8719 | Yes | 27125.6371 | 1 | 129.1795 | 45.2128 | 0.49996 | 0 | - | 0.37158
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 1065.7308 | Yes | 13986.6566 | 1 | 861.1966 | 301.4188 | 1.3999 | 40.0456 | 26.6129 | 1.3934
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 5134.8849 | Yes | 67390.2547 | 1 | 2282.1711 | 798.7599 | 1.3999 | 40.0456 | 128.2258 | 1.3934
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 1065.7308 | Yes | 13986.6566 | 1 | 861.1966 | 301.4188 | 1.3999 | 40.0456 | 26.6129 | 1.3934
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 5134.8849 | Yes | 67390.2547 | 1 | 2282.1711 | 798.7599 | 1.3999 | 40.0456 | 128.2258 | 1.3934
CORRIDOR_POD_3_ZN_1_FLR_1 | 2066.8719 | Yes | 27125.6371 | 1 | 129.1795 | 45.2128 | 0.49996 | 0 | - | 0.37158
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 1065.7308 | Yes | 13986.6566 | 1 | 861.1966 | 301.4188 | 1.3999 | 40.0456 | 26.6129 | 1.3934
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 3390.9617 | Yes | 44502.9984 | 1 | 1507.0941 | 527.4829 | 1.3999 | 40.0456 | 84.6774 | 1.3934
COMPUTER_CLASS_ZN_1_FLR_1 | 1743.9232 | Yes | 22887.2563 | 1 | 775.077 | 271.2769 | 1.3999 | 40.0456 | 43.5484 | 1.8579
MAIN_CORRIDOR_ZN_1_FLR_1 | 5877.667 | Yes | 77138.5306 | 1 | 387.5385 | 135.6385 | 0.49996 | 0 | - | 0.37158
LOBBY_ZN_1_FLR_1 | 1840.8078 | Yes | 24158.7706 | 1 | 818.1368 | 286.3479 | 1.2999 | 0 | - | 0.37158
MECH_ZN_1_FLR_1 | 2712.7694 | Yes | 35602.3987 | 1 | 0 | 0 | 1.4999 | 0 | - | 0.92894
BATH_ZN_1_FLR_1 | 2045.342 | Yes | 26843.0784 | 1 | 430.5983 | 150.7094 | 0.89991 | 0 | - | 0.37158
OFFICES_ZN_1_FLR_1 | 4747.3464 | Yes | 62304.1978 | 1 | 1808.5129 | 632.9795 | 1.0999 | 200.0129 | 23.7352 | 1.0033
GYM_ZN_1_FLR_1 | 3843.09 | Yes | 50436.7315 | 1 | 732.0171 | 400.2411 | 1.3999 | 33.3714 | 115.1613 | 0.46447
KITCHEN_ZN_1_FLR_1 | 1808.5129 | Yes | 23734.9325 | 1 | 344.4787 | 120.5675 | 1.1999 | 66.958 | 27.0096 | 151.1148
CAFETERIA_ZN_1_FLR_1 | 3390.9617 | Yes | 44502.9984 | 1 | 1550.1539 | 542.5539 | 0.89991 | 10.0114 | 338.7097 | 2.3586
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 4295.2182 | Yes | 56370.4646 | 1 | 1722.3933 | 602.8376 | 1.2999 | 100.0065 | 42.9494 | 1.3934
TOTAL | 73966.0258 |  | 970730.4826 |  | 27041.5743 | 9608.5861 |  |  | 1476.5975
AREA WEIGHTED AVERAGE | [6 empty] | 1.1874 | 42.6171 |  | 4.7985

## Outdoor Air
Minimum Outdoor Ventilation Air Requirements
|  |  |  | Total Occupants | Total OSA Ventilation (cfm/zone) |  |  | Total OSA Ventilation (cfm/ft2)
Zone | Area (ft2) | Multipliers | Assumed Space Type | 62.1-2004 | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007) | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007)
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 1065.735 | 1 | Classrooms (ages 5-8) | 24.75 | 399.6506 | 394.3219 | 394.3219 | 0.375 | 0.37 | 0.37
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 5134.905 | 1 | Classrooms (ages 5-8) | 119.25 | 1925.5894 | 1899.9149 | 1899.9149 | 0.375 | 0.37 | 0.37
CORRIDOR_POD_1_ZN_1_FLR_1 | 2066.88 | 1 | Corridors (school) | 0 | 206.688 | 124.0128 | 124.0128 | 0.1 | 0.06 | 0.06
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 1065.735 | 1 | Classrooms (ages 5-8) | 24.75 | 399.6506 | 394.3219 | 394.3219 | 0.375 | 0.37 | 0.37
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 5134.905 | 1 | Classrooms (ages 5-8) | 119.25 | 1925.5894 | 1899.9149 | 1899.9149 | 0.375 | 0.37 | 0.37
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 1065.735 | 1 | Classrooms (ages 5-8) | 24.75 | 399.6506 | 394.3219 | 394.3219 | 0.375 | 0.37 | 0.37
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 5134.905 | 1 | Classrooms (ages 5-8) | 119.25 | 1925.5894 | 1899.9149 | 1899.9149 | 0.375 | 0.37 | 0.37
CORRIDOR_POD_2_ZN_1_FLR_1 | 2066.88 | 1 | Corridors (school) | 0 | 206.688 | 124.0128 | 124.0128 | 0.1 | 0.06 | 0.06
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 1065.735 | 1 | Classrooms (ages 5-8) | 24.75 | 399.6506 | 394.3219 | 394.3219 | 0.375 | 0.37 | 0.37
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 5134.905 | 1 | Classrooms (ages 5-8) | 119.25 | 1925.5894 | 1899.9149 | 1899.9149 | 0.375 | 0.37 | 0.37
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 1065.735 | 1 | Classrooms (ages 5-8) | 24.75 | 399.6506 | 394.3219 | 394.3219 | 0.375 | 0.37 | 0.37
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 5134.905 | 1 | Classrooms (ages 5-8) | 119.25 | 1925.5894 | 1899.9149 | 1899.9149 | 0.375 | 0.37 | 0.37
CORRIDOR_POD_3_ZN_1_FLR_1 | 2066.88 | 1 | Corridors (school) | 0 | 206.688 | 124.0128 | 124.0128 | 0.1 | 0.06 | 0.06
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 1065.735 | 1 | Classrooms (ages 5-8) | 24.75 | 399.6506 | 394.3219 | 394.3219 | 0.375 | 0.37 | 0.37
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 3390.975 | 1 | Classrooms (ages 5-8) | 78.75 | 1271.6156 | 1254.6608 | 1254.6608 | 0.375 | 0.37 | 0.37
COMPUTER_CLASS_ZN_1_FLR_1 | 1743.93 | 1 | Computer Lab. | 48.6486 | 653.9737 | 645.2541 | 645.2541 | 0.375 | 0.37 | 0.37
MAIN_CORRIDOR_ZN_1_FLR_1 | 5877.69 | 1 | Corridors (school) | 0 | 587.769 | 352.6614 | 352.6614 | 0.1 | 0.06 | 0.06
LOBBY_ZN_1_FLR_1 | 1840.815 | 1 | Corridors (school) | 0 | 184.0815 | 110.4489 | 110.4489 | 0.1 | 0.06 | 0.06
MECH_ZN_1_FLR_1 | 2712.78 | 1 |  | 0 | NA | NA | NA | NA | NA | NA
BATH_ZN_1_FLR_11. | 2045.35 | 1 | Restroom | 0 | 0 | 0 | 0 | 0 | 0 | 0
OFFICES_ZN_1_FLR_1 | 4747.365 | 1 | Office space | 22.05 | 474.7365 | 403.526 | 403.526 | 0.1 | 0.085 | 0.085
GYM_ZN_1_FLR_1 | 3843.105 | 1 | Gym, stadium (play area) | 107.2072 | 2305.863 | 1152.9315 | 1152.9315 | 0.6 | 0.3 | 0.3
KITCHEN_ZN_1_FLR_1 | 1808.52 | 1 | Kitchen | 25.1874 | 5000 | 5000 | 5000 | 2.7647 | 2.7647 | 2.7647
CAFETERIA_ZN_1_FLR_1 | 3390.975 | 1 | Cafeteria / fast food dining | 315 | 6781.95 | 3153.6068 | 3153.6068 | 2 | 0.93 | 0.93
LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 4295.235 | 1 | Libraries | 91.7241 | 644.2853 | 730.19 | 730.19 | 0.15 | 0.17 | 0.17
TOTAL | 73966.315 |  |  | 1433.3174 | 30550.1893 | 25040.8237 | 25040.8237 | 0.41303 | 0.33854 | 0.33854
Space Type Lookup
Art classroom
Auditorium seating area
Bank vaults/safe deposit
Barber shop
Barracks sleeping areas
Bars, cocktail lounges
Beauty and nail salons
Bedroom/Living Room (hotel/motel/dorm)
Booking/waiting
Bowling alley (seating)
Cafeteria / fast food dining
Cell
Classrooms (age 9 plus)
Classrooms (ages 5-8)
Coin operated laundries
Computer (not printing)
Computer Lab.
Conference / meeting
Corridors (school)
Corridors (public spaces)
Courtrooms
Daycare (through age 4)
Dayroom
Disco/dance floors
Gambling casinos
Game arcades
Guard stations
Gym, stadium (play area)
Health club/aerobics room
Health club/weight rooms
Kitchen
Lecture Classroom
Lecture Hall (fixed seats)
Legislative chambers
Libraries
Lobbies
Lobbies/prefunction (hotel, motel, resort, dorm)
Main entry lobbies (office bldgs)3.
Mall common areas
Media Center
Multi-purpose assembly (hotel, motel, resort, dorm)
Multi-use Assembly (school)
Museums (Children’s)
Museums/Galleries
Music/theater/dance
Office space
Pet shops (animal areas)
Pharmacy (prep. area)
Photo studios
Places of religious worship
Reception areas
Restaurant dining rooms
Restroom
Sales (except as below)
Science laboratories
Shipping/Receiving
Spectator areas
Sports arena (play area)
Stages, studios
Storage rooms
Supermarket
Swimming (pool & deck)
Telephone/data entry
Transportation waiting
Warehouses
Wood/metal shop
Residiential single bedroom apartment
Commercial laundry
Patient rooms
Medical procedure
Operating rooms
Recovery and ICU
Autopsy rooms
Physical therapy

## Schedules
Schedule | Type | Through | Day of Week | 1 am | 2 am | 3 am | 4 am | 5 am | 6 am | 7 am | 8 am | 9 am | 10 am | 11 am | Noon | 1 pm | 2 pm | 3 pm | 4 pm | 5 pm | 6 pm | 7 pm | 8 pm | 9 pm | 10 pm | 11 pm | 12 pm
Internal Loads Schedules
BLDG_LIGHT_SCH | Fraction | 1/1 - 6/30 and 9/1-12/31 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
(Study Periods) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
BLDG_LIGHT_SCH | Fraction | 6/30 - 9/1 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
(Summer Holiday) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
BLDG_EQUIP_SCH | Fraction | 1/1 - 6/30 and 9/1-12/31 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
(Study Periods) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
BLDG_EQUIP_SCH | Fraction | 6/30 - 9/1 | WD, SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
(Summer Holiday) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Kitchen_Elec_EQUIP_SCH | Fraction | 1/1 - 6/30 and 9/1-12/31 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
(Study Periods) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Kitchen_Elec_EQUIP_SCH | Fraction | 6/30 - 9/1 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
(Summer Holiday) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Kitchen_Gas_EQUIP_SCH | Fraction | 1/1 - 6/30 and 9/1-12/31 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
(Study Periods) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
Kitchen_Gas_EQUIP_SCH | Fraction | 6/30 - 9/1 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
(Summer Holiday) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
BLDG_OCC_SCH | Fraction | 1/1 - 6/15 and 9/15-12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
(Study Periods) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH | Fraction | 6/15 - 9/15 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
(Summer Holiday) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_Extend | Fraction | 1/1 - 6/30 and 9/1-12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
(Study Periods) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_Extend | Fraction | 6/30 - 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0
(Summer Holiday) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Offices | Fraction | 1/1 - 6/30 and 9/1-12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
(Study Periods) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Offices | Fraction | 6/30 - 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
(Summer Holiday) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Gym | Fraction | 1/1 - 6/30 and 9/1-12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
(Study Periods) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Gym | Fraction | 6/30 - 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0
(Summer Holiday) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Cafeteria | Fraction | 1/1 - 6/30 and 9/1-12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0
(Study Periods) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Cafeteria | Fraction | 6/30 - 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0
(Summer Holiday) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Service Water Heater Load Schedule
BLDG_SWH_SCH | Fraction | Through 6/15 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0
(Study Periods) |  |  | SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
|  |  | WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
|  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_SWH_SCH | Fraction | Through 9/15 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0 | 0
(Summer Holiday) |  |  | SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.65 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
|  |  | WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
|  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Infiltration Schedule
INFIL_SCH_PNNL | fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
|  |  | Sat, Sun, Hol, WinterDesign, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
INFIL_Door_Opening_SCH | fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | varies | [6 empty] | 1 | varies |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat, Sun, Hol, AllOtherDays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVAC Schedules
HVACOperationSchd | on/off | Through 12/31 | WD, SummerDesign, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
|  |  | Sat, Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FAN_SCH | AnyNumber | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
ReheatCoilAvailSched | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
CoolingCoilAvailSched | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
MinOA_MotorizedDamper_Sched | fraction | Through 12/31 | WD, SummerDesign, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
|  |  | Sat, Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Sched | fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
| (°C) |  | SummerDesign, Sat, Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
CLGSETP_SCH | Temperature | Through 12/31 | WD | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7
| (°C) |  | SummerDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  |  | WinterDesign, Sat, Sun, Hol, Other | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
HTGSETP_SCH_SETBACk | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
(For mechanical room and bathroom) | (°C) |  | SummerDesign, Sat, Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
CLGSETP_SCH_SETUP | Temperature | Through 12/31 | WD | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
(For mechanical room and bathroom) | (°C) |  | SummerDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  |  | WinterDesign, Sat, Sun, Hol, Other | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
VAV-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
HTGSETP_SCH | Temperature | Through 12/31 | WD | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 64.04 | 68 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 60.08 | 60.08 | 60.08
| (°F) |  | SummerDesign, Sat, Sun, Hol, Other | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
|  |  | WinterDesign | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8
CLGSETP_SCH | Temperature | Through 12/31 | WD | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 78.08 | 77 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 80.06 | 80.06 | 80.06
| (°F) |  | SummerDesign | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2
|  |  | WinterDesign, Sat, Sun, Hol, Other | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06
HTGSETP_SCH_SETBACk | Temperature | Through 12/31 | WD | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
(For mechanical room and bathroom) | (°F) |  | SummerDesign, Sat, Sun, Hol, Other | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
|  |  | WinterDesign | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8
CLGSETP_SCH_SETUP | Temperature | Through 12/31 | WD | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06
(For mechanical room and bathroom) | (°F) |  | SummerDesign | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2
|  |  | WinterDesign, Sat, Sun, Hol, Other | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06
VAV-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6
Heat-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8
Notes: | 1. For climate zones other than 1B, 2B, and 3B occupied cooling thermostat setpoints are maintained continuously (no setback). 2. These schedules reflect optimum start controls. For systems less than 10,000 cfm there is no optimal start and full occupied temperature setpoints begin two hours prior to occupancy instead of being ramped up incrementally beginning two hours prior to occupancy.

## SchedulePlots
Primary School: Weekday Schedules