## Building Description
ASHRAE 90.1 Prototype Building Modeling Specifications
Pacific Northwest National Laboratory, updated on 03-21-2014
| Item | Descriptions |  |  | Data Source
Program
| Vintage | NEW CONSTRUCTION
| Location (Representing All 17 Climate Zones) | Zone 1A: Miami (very hot, humid) Zone 1B: Riyadh, Saudi Arabia (very hot, dry) Zone 2A: Houston (hot, humid) Zone 2B: Phoenix (hot, dry) Zone 3A: Memphis (warm, humid) Zone 3B: El Paso (warm, dry) Zone 3C: San Francisco (warm,marine) | Zone 4A: Baltimore (mild, humid) Zone 4B: Albuquerque (mild, dry) Zone 4C: Salem (mild, marine) Zone 5A: Chicago (cold, humid) Zone 5B: Boise (cold, dry) Zone 5C: Vancouver, BC (cold, marine) | Zone 6A: Burlington (cold, humid) Zone 6B: Helena (cold, dry) Zone 7: Duluth (very cold) Zone 8: Fairbanks (subarctic) | Selection of representative climates based on Briggs' paper
| Available fuel types | gas, electricity
| Building Type (Principal Building Function) | Non-refrigerated warehouse
| Building Prototype | WAREHOUSE
Form
| Total Floor Area (sq feet) | 49,495 (330 ft x 150 ft)
Building shape
| Aspect Ratio | 2.2
| Number of Floors | 1
| Window Fraction (Window-to-Wall Ratio) | 0.71% Punched windows in Office Space
| Window Locations | Only for Office Space
| Shading Geometry | none
| Azimuth | non-directional
| Thermal Zoning | Three zones: Bulk Storage, Fine Storage, and Office. The Office zone is enclosed on two sides and at the top by the Fine Storage zone.
| Floor to floor height (feet) | 28
| Floor to ceiling height (feet) | 14 (Office)
| Glazing sill height (feet) | 3 (top of the window is 8 ft high with 5 ft high glass)
Architecture
Exterior walls
| Construction | Metal Building Wall Metal Surface + Wall Insulation + Gypsum Board |  |  | Construction type: 2003 CBECS Data and PNNL's CBECS Study 2007. Exterior wall layers: default 90.1 layering
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | ASHRAE 90.1 Requirements Nonresidential; Walls, Above-Grade, Metal Building Semi heated; Walls, Above-Grade, Metal Building |  |  | ASHRAE 90.1
| Dimensions | based on floor area and aspect ratio
| Tilts and orientations | vertical
Roof
| Construction | Metal Building Roof Metal Surface + Roof Insulation |  |  | Construction type: 2003 CBECS Data and PNNL's CBECS Study 2007. Roof layers: default 90.1 layering
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | ASHRAE 90.1 Requirements Nonresidential; Roofs, Metal Building Semi heated; Roofs, Metal Building |  |  | ASHRAE 90.1
| Dimensions | based on floor area and aspect ratio
| Tilts and orientations | horizontal
Window
| Dimensions | based on window fraction, location, glazing sill height, floor area and aspect ratio
| Glass-Type and frame | Hypothetical window with weighted U-factor and SHGC
| U-factor (Btu / h * ft2 * °F) | ASHRAE 90.1 Requirements Nonresidential; Vertical Glazing |  |  | ASHRAE 90.1
SHGC (all)
Visible transmittance
| Operable area | 0
Skylight
| Dimensions | Bulk Storage, Fine Storage Rectangular Skylights (4 ft x 4 ft) = 16 ft2 per skylight Number of skylights and total skylight area vary according to ASHRAE 90.1 Requirements |  |  | ASHRAE 90.1
| Glass-Type and frame | Hypothetical glass and frame meeting ASHRAE 90.1 Requirements below
| U-factor (Btu / h * ft2 * °F) | ASHRAE 90.1 Requirements Nonresidential; Skylight with Curb, Glass |  |  | ASHRAE 90.1
SHGC (all)
Visible transmittance
Foundation
| Foundation Type | Slab-on-Grade
| Construction | 6" concrete slab
| Thermal properties for ground level floor U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | ASHRAE 90.1 Requirements Nonresidential; Slab-on-Grade Floors, unheated Semi heated; Slab-on-Grade Floors, unheated |  |  | ASHRAE 90.1
| Thermal properties for basement walls | NA
| Dimensions | based on floor area and aspect ratio
Interior Partitions
| Construction | 2 x 4 uninsulated steel stud wall
| Dimensions | based on floor plan and floor-to-floor height
| Internal Mass | Bulk Storage Material 12.5 lb/sf, 8ft thick, area of 64,890 ft2
Air Barrier System
| Infiltration | office: 0.043346 cfm/ft2 of exterior surface area fine storage: 0.044442 cfm/ft2 of exterior surface area bulk storage: 3265 cfm (fixed)
HVAC
System Type
| Heating type | Gas furnace inside the packaged air conditioning unit |  |  | 2003 CBECS Data, PNNL's CBECS Study 2006, and 90.1 Mechanical Subcommittee input.
| Cooling type | Packaged air conditioning unit
| Distribution and terminal units | Direct, uncontrolled air
HVAC Sizing
| Air Conditioning | autosized to design day
| Heating | autosized to design day
HVAC Efficiency
| Air Conditioning | Various by climate location and design cooling capacity ASHRAE 90.1 Requirements Minimum equipment efficiency for Air Conditioners and Condensing Units |  |  | ASHRAE 90.1
| Heating | Various by climate location and design heating capacity ASHRAE 90.1 Requirements Minimum equipment efficiency for Warm Air Furnaces
HVAC Control
| Thermostat Setpoint | Fine storage: 80°F Cooling/ 60°F Heating; Office Area: 75°F Cooling/ 70°F Heating; Bulk Storage: 50°F Heating;
| Thermostat Setback | 85°F Cooling/60°F Heating
| Supply air temperature | Minimum 55°F, maximum 110°F
| Chilled water supply temperatures | NA
| Hot water supply temperatures | NA
| Economizers | Various by climate location and cooling capacity Control type: differential dry bulb |  |  | ASHRAE 90.1
| Ventilation | ASHRAE Ventilation Standard 62.1 See under Outdoor Air |  |  | ASHRAE Ventilation Standard 62.1
| Demand Control Ventilation | No |  |  | ASHRAE 90.1
| Energy Recovery | No |  |  | ASHRAE 90.1
Supply Fan
| Fan schedules | See under Schedules
| Supply Fan Total Efficiency (%) | Varies depending on fan motor size |  |  | ASHRAE 90.1 requirements for motor efficiency and fan power limitation
| Supply Fan Pressure Drop | Various depending on the fan supply air cfm
Pump
| Pump Type | NA
| Rated Pump Head | NA
| Pump Power | NA
Cooling Tower
| Cooling Tower Type | NA
| Cooling Tower Power | NA
Service Water Heating
| SWH type | Storage Tank
| Fuel type | Electricity
| Thermal efficiency (%) | 1
| Tank Volume (gal) | 20
| Water temperature setpoint | 140 F |  |  | Reference: PNNL 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Water consumption | See under Schedules
Internal Loads & Schedules
Lighting
| Average power density (W/ft2) | ASHRAE 90.1 Lighting Power Densities Using the Space-By-Space Method See under Zone Summary |  |  | ASHRAE 90.1
| Schedule | See under Schedules
| Daylighting Controls | ASHRAE 90.1 Requirements
| Occupancy Sensors | ASHRAE 90.1 Requirements
Plug load
| Average power density (W/ft2) | See under Zone Summary |  |  | User's Manual for ASHRAE Standard 90.1-2004 (Appendix G)
| Schedule | See under Schedules
Occupancy
| Average people | See under Zone Summary |  |  | User's Manual for ASHRAE Standard 90.1-2004 (Appendix G)
| Schedule | See under Schedules
Misc.
Elevator
| Peak Power | Not modeled
| Schedule | Not modeled
Exterior Lighting
| Peak Power | ASHRAE 90.1 Lighting Power Densities For Building Exteriors |  |  | ASHRAE 90.1
| Schedule | See under Schedules
References
Briggs, R.S., R.G. Lucas, and Z.T. Taylor. 2003. Climate Classification for Building Energy Codes and Standards: Part 2—Zone Definitions, Maps, and Comparisons. ASHRAE Transactions 109(2).
McGraw-Hill Companies, Inc. (2001). Time-Saver Standards for Building Types. New York, NY.
LBNL (1991). Huang, Joe, Akbari, H., Rainer, L. and Ritschard, R. 481 Prototypical Commercial Buildings for 20 Urban Market Areas, prepared for the Gas Research Institute, Chicago IL, also LBL-29798, Berkeley CA.
PNNL's CBECS Study. 2007. Analysis of Building Envelope Construction in 2003 CBECS Buildings. Dave Winiarski, Mark Halverson, and Wei Jiang. Pacific Northwest National Laboratory. March 2007.
PNNL's CBECS Study. 2006. Review of Pre- and Post-1980 Buildings in CBECS – HVAC Equipment. Dave Winiarski, Wei Jiang and Mark Halverson. Pacific Northwest National Laboratory. December 2006.
PNNL. 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models. Pacific Northwest National Laboratory, Richland, Washington. Available at https://www.energycodes.gov/development/commercial/90.1_models.

## Zone Summary
Zone Summary
(90.1-2004 baseline requirements for LPD)
Zone | Area [ft²] | Conditioned [Y/N] | Volume [ft³] | Multipliers | Gross Wall Area [ft²] | Window Glass Area [ft²] | Lighting [W/ft²] | People [ft²/person] | Number of People | Plug and Process [W/ft²]
ZONE1 OFFICE | 2550.0032 | Yes | 35699.502 | 1 | 1610.0071 | 190.1092 | 0.9999 | 510.0437 | 4.9996 | 0.75
ZONE2 FINE STORAGE | 15000 | Yes | 384300 | 1 | 8189.98 | 0 | 0.79992 | 0 | - | -
ZONE3 BULK STORAGE | 34499.9677 | Yes | 1245987.0024 | 1 | 17080.0052 | 159.9673 | 0.79992 | 0 | - | 0.23769
TOTAL | 52049.9709 |  | 1665986.5044 |  | 26879.9922 | 350.0764 |  |  | 4.9996
AREA WEIGHTED AVERAGE | [6 empty] | 0.80972 | 24.9878 |  | 0.19429

## Outdoor Air
Minimum Outdoor Ventilation Air Requirements
|  |  |  | Total Occupants | Total OSA Ventilation (cfm/zone) |  |  | Total OSA Ventilation (cfm/sqft)
Zone | Area (sqft) | Multipliers | Assumed Space Type | 62.1-20041 | 62-1999 | 62.1-2004 | 90.1-2010 (62.1-2007) | 62-1999 | 62.1-2004 | 90.1-2010 (62.1-2007)
ZONE1 OFFICE | 2550.0132 | 1 | Office space | 12.7501 | 255.0013 | 216.7511 | 216.7511 | 0.1 | 0.085 | 0.085
ZONE2 FINE STORAGE | 15000.0587 | 1 | Warehouses | 0 | 750.0029 | 900.0035 | 900.0035 | 0.05 | 0.06 | 0.06
ZONE3 BULK STORAGE | 34500.1026 | 1 | Warehouses | 0 | 1725.0051 | 2070.0062 | 2070.0062 | 0.05 | 0.06 | 0.06
TOTAL | 52050.1745 |  |  | 12.7501 | 2730.0094 | 3186.7608 | 3186.7608 | 0.05245 | 0.061225 | 0.061225
1. Warehouse occupancy density is not included in ASHRAE 62.1-2004, therefore assuming no occupancy density in fine and bulk storage spaces. This assumption is also aligned with AEDG-Warehouse project committee's recommendation.

## Schedules
Schedule | Type | Through | Day of Week | 1 am | 2 am | 3 am | 4 am | 5 am | 6 am | 7 am | 8 am | 9 am | 10 am | 11 am | Noon | 1 pm | 2 pm | 3 pm | 4 pm | 5 pm | 6 pm | 7 pm | 8 pm | 9 pm | 10 pm | 11 pm | 12 pm
Internal Loads Schedules
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD (Office Light WD Sensor) | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.23 | 0.42 | 0.77 | 0.77 | 0.77 | 0.77 | 0.68 | 0.77 | 0.77 | 0.77 | 0.77 | 0.61 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
|  |  | WEH (Office Light WEH) | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
|  |  | WD (Storage Light WD) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.6 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.75 | 0.6 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  |  | WEH (Storage Light WEH) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD (Office_Plug_WD_BASE) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  |  | WEH (Office_Plug_WEH_BASE) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  |  | WD (Bulk Storage Plug WD) | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  | WEH (Bulk Storage Plug WEH) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH | Fraction | Through 12/31 | WD (Office Occ WD) | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.21 | 1 | 1 | 1 | 1 | 0.53 | 1 | 1 | 1 | 1 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | WEH (Office Occ WEH) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Service Water Heater Load Schedule
BLDG_SWH_SCH | Fraction | Through 12/31 | WD (Office DHW WD) | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.101 | 0.399 | 0.501 | 0.501 | 0.696 | 0.9 | 0.798 | 0.696 | 0.798 | 0.297 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | WEH (Office DHW WEH) | 0 | 0 | 0 | 0 | 0 | 0 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0 | 0 | 0 | 0 | 0 | 0
Infiltration Schedule
INFIL_SCH_PNNL | fraction | Through 12/31 | WD (Office Infiltration WD) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.25 | 1.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1.25 | 1.25 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WEH (Office infiltration WEH) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WD (Fine Storage INFIL WD) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.25 | 1.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1.25 | 1.25 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WEH (Fine Storage INFIL WEH) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WD (Bulk Storage INFIL_Base WD) | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 1 | 1 | 1 | 1 | 0.765 | 1 | 1 | 1 | 1 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765
|  |  | WEH (Bulk Storage INFIL_Base WEH) | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765
HVAC Schedules
HVACOperationSchd | on/off | Through 12/31 | Compact HVAC-Always 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Fan Schedule | on/off | Through 12/31 | WD (FanSched) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | WEH (FanSched) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesignDay (FanSched) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesignDay (FanSched) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
MinOA_Sched | On/Off | Through 12/31 | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
MinOA_MotorizedDamper_Sched | fraction | Through 12/31 | WD, Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HTGSETP_SCH | Temperature | Through 12/31 | WD (Office Heating WD) | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
| (°C) |  | WEH (Office Heating WEH) | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
CLGSETP_SCH | Temperature | Through 12/31 | WD (Office Cooling WD) | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
| (°C) |  | WEH (Office Cooling WEH) | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
Bulk Storage Heating Setpoint Schedule | Temperature | Through 12/31 | AllDays | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
(°C)
Hot Water Setpoint Temp Schedule (SWH) | Temperature | Through 12/31 | AllDays | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
(°C)
Fine Storage Heating Setpoint Schedule | Temperature | Through 12/31 | AllDays | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
(°C)
Fine Storage Cooling Setpoint Schedule | Temperature | Through 12/31 | AllDays | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
(°C)
HTGSETP_SCH | Temperature | Through 12/31 | WD (Office Heating WD) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 64.94 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
| (°F) |  | WEH (Office Heating WEH) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
CLGSETP_SCH | Temperature | Through 12/31 | WD (Office Cooling WD) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 80.06 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
| (°F) |  | WEH (Office Cooling WEH) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Bulk Storage Heating Setpoint Schedule | Temperature | Through 12/31 | AllDays | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
(°F)
Hot Water Setpoint Temp Schedule | Temperature | Through 12/31 | AllDays | 120.02 | 120.02 | 120.02 | 120.02 | 120.02 | 120.02 | 120.02 | 120.02 | 120.02 | 120.02 | 120.02 | 120.02 | 120.02 | 120.02 | 120.02 | 120.02 | 120.02 | 120.02 | 120.02 | 120.02 | 120.02 | 120.02 | 120.02 | 120.02
(°F)
Fine Storage Heating Setpoint Schedule | Temperature | Through 12/31 | AllDays | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008 | 60.008
(°F)
Fine Storage Cooling Setpoint Schedule | Temperature | Through 12/31 | AllDays | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06
(°F)