## Baseline Description
Prototype Building Modeling Specifications
Pacific Northwest National Laboratory, updated on October 18, 2018
| Item | Descriptions |  |  | Data Source
Program
| Vintage | NEW CONSTRUCTION
| Location (Representing 8 Climate Zones) | Zone 1A: Honolulu, Hawaii (very hot, humid) Zone 1B: New Delhi, India (very hot, dry) Zone 2A: Tampa, Florida (hot, humid) Zone 2B: Tucson, Arizona (hot, dry) Zone 3A: Atlanta, Georgia (warm, humid) Zone 3B: El Paso, Texas (warm, dry) Zone 3C: San Diego, California (warm, marine) | Zone 4A: Baltimore (mild, humid) Zone 4B: Albuquerque (mild, dry) Zone 4C: Salem (mild, marine) Zone 5A: Chicago (cold, humid) Zone 5B: Boise (cold, dry) Zone 5C: Vancouver, BC (cold, marine) | Zone 6A: Burlington (cold, humid) Zone 6B: Helena (cold, dry) Zone 7: Duluth (very cold) Zone 8: Fairbanks (subarctic) | Selection of representative climates based on ASHRAE Standard 169-2013
| Available fuel types | Gas, electricity
| Building Type (Principal Building Function) | Health Care
| Building Prototype | Hospital
Form
| Total Floor Area (sq feet) | 241,410 (including basement) |  |  | Reference: Time Saver Standards; Hospital studies (ConEd, EPRI, MEOS, LBL) cited in Huang et al. 1991
Building shape
| Aspect Ratio | 1.31 (230 ft x 175 ft for each floor)
| Number of Floors | 5 (plus basement)
| Window Fraction (Window-to-Wall Ratio) | North: 12%, East: 13%, South: 15%, West: 24% Average Total: 16%
| Window Locations | See pictures
| Shading Geometry | none
| Azimuth | non-directional
| Thermal Zoning | See Zone Summary and HVAC Zoning for thermal zoning layout, including Emergency Room, Office, Lobby, Nurse Station, Operating Room, Patient Room, Physical Therapy, Lab, Radiology, Dining, Kitchen, and Corridors. Percentages of floor area: Clinic 25%, Core/Public 35%, Perimeter (patient rooms and offices) 15%, Kitchen 5%, Lobby/Hallway 20% |  |  | Reference: Time Saver Standards; Hospital studies (ConEd, EPRI, MEOS, LBL) cited in Huang et al. 1991
| Floor to floor height (ft) | 14 ft above ground 8 ft basement
| Floor to ceiling height (ft) | 14 ft above ground and 8 ft basement (no drop-in ceiling plenum is modeled)
| Glazing sill height (ft) | 3 ft (4 ft high windows)
Architecture
Exterior walls
| Construction | Mass (concrete blocks): 8 in. HW concrete+wall insulation+0.5 in. gypsum board |  |  | Construction type: 2003 CBECS Data and PNNL's CBECS Study 2007. Base assembly from 90.1 Appendix A.
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | 1st, 2nd and 5th floors: use nonresidential envelop requirement 3rd and 4th floors: use residential envelop requirement since most of the spaces in the perimeter zones are patient rooms, which are residential spaces based on definitions in the codes and standards |  |  | Applicable codes or standards
| Dimensions | Based on floor area and aspect ratio
| Tilts and orientations | Vertical
Roof
| Construction | Built-up Roof: roof membrane+roof insulation+metal decking |  |  | Construction type: 2003 CBECS Data and PNNL's CBECS Study 2007. Base assembly from 90.1 Appendix A.
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; roofs, insulation entirely above deck |  |  | Applicable codes or standards
| Dimensions | Based on floor area and aspect ratio
| Tilts and orientations | Horizontal
Window
| Dimensions | Based on window fraction, location, glazing sill height, floor area and aspect ratio
| Glass-Type and frame | Hypothetical window with a weighted U-factor and SHGC
| U-factor (Btu / h * ft2 * °F) | Requirements in codes or standards |  |  | Applicable codes or standards
SHGC (all)
| Visible transmittance | Same as above requirements
| Operable area | 0
Skylight
| Dimensions | Not modeled
| Glass-Type and frame | NA
U-factor (Btu / h * ft2 * °F)
SHGC (all)
Visible transmittance
Foundation
| Foundation Type | Basement (conditioned)
| Construction | 8" concrete wall; 8" concrete slab, 140 lbs heavy-weight aggregate
| Thermal properties for basement walls | Requirements in codes or standards |  |  | Applicable codes or standards
| Dimensions | Based on floor area and aspect ratio
Interior Partitions
| Construction | 2 x 4 uninsulated stud wall
| Dimensions | Based on floor plan and floor-to-floor height
| Internal Mass | 6 inches standard wood (16.6 lb/ft²)
Air Barrier System
| Infiltration (ACH) | Peak: 0.2016 cfm/sf of above grade exterior wall surface area, adjusted by wind (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) |  |  | Reference: PNNL-18898. Infiltration Modeling Guidelines for Commercial Building Energy Analysis. Modeled peak infiltration rate may be different for different codes or standards because of their continuous air barrier requirements.
HVAC
System Type
| Heating type | Gas boiler |  |  | 2003 CBECS Data, PNNL's CBECS Study 2007, and 90.1 Mechanical Subcommittee input.
| Cooling type | Two water cooled chillers
| Distribution and terminal units | See HVAC Zoning Medical critical zones: five air handling unit systems with hot water reheating and electric stream humidifiers, either CAV or VAV with reheat depending on codes and standards Non-critical zones: two VAV systems for general zones and one constant air volume (CAV) system for kitchen zone: VAV terminal box with damper and hot water reheating coil; minimum VAV terminal flow fraction dependent on codes and standards. |  |  | AEDG for Small Healthcare Facilities Applicable codes or standards
HVAC Sizing
| Air Conditioning | Autosized to design day
| Heating | Autosized to design day
HVAC Efficiency
| Cooling | Chiller efficiency varies by climate location and design cooling capacity Requirements in codes or standards |  |  | Applicable codes or standards
| Heating | Boiler efficiency varies by climate location and design heating capacity Requirements in codes or standards
HVAC Control
| Thermostat Setpoint | 75°F Cooling/70°F Heating
| Thermostat Setback | No setback
| Supply air temperature | Maximum 104F, Minimum 52F |  |  | Temperature reset may be used if required by applicable codes or standards
| Chilled water supply temperatures | 44 F |  |  | Temperature reset may be used if required by applicable codes or standards
| Hot water supply temperatures | 180 F
| Economizers | Requirements in codes or standards |  |  | Input from 90.1 Mechanical Subcommittee
| Ventilation | ASHRAE Standard 62.1, International Mechanical Code, AIA Guidelines for Design and Construction of Health Care Facilities See Outdoor&Supply Air. |  |  | AIA Guidelines for Design and Construction of Hospital and Health Care Facilities ASHRAE Standard 62.1 International Mechanical Code
| Demand Control Ventilation | Requirements in codes or standards |  |  | Applicable codes or standards
| Energy Recovery | Requirements in codes or standards |  |  | Applicable codes or standards
Supply Fan
| Fan schedules | See under Schedules
| Supply Fan Total Efficiency (%) | Depending on the fan motor size and requirements in codes or standards |  |  | Requirements in applicable codes or standards for motor efficiency and fan power limitation
| Supply Fan Pressure Drop | Depending on the fan supply air cfm
Pump
| Pump Type | Primary chilled water (CHW) pumps constant speed; secondary CHW pump: variable speed; cooling tower pump: variable speed: service hot water (SWH): constant speed; hot water (HW) pump: variable speed
| Rated Pump Head | Pump power assumptions as specified in ASHRAE 90.1 Appendix G |  |  | ASHRAE 90.1
| Pump Power | Autosized
Cooling Tower
| Cooling Tower Type | Open cooling tower with two-speed fans
| Cooling Tower Power | Autosized
Service Water Heating
| SWH type | Main and central gas water heater with storage tank Electric dishwasher booster water heater Gas water heater for laundry with storage |  |  | Reference: PNNL-23269 Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Fuel type | Natural Gas (main and laundry); Electric (dishwasher booster) |  |  | Reference: PNNL-23269 Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Thermal efficiency (%) | Requirements in codes or standards |  |  | Applicable codes or standards
| Tank Volume (gal) | 600 (main); 300 (laundry); 6 (dishwasher booster) |  |  | Reference: PNNL-23269 Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Water temperature setpoint | 140 F (main), 180 F (laundry and dishwasher booster)
| Water consumption | See under Schedules
Internal Loads & Schedules
Lighting
| Average power density (W/ft2) | Requirements in codes or standards See Zone Summary |  |  | Applicable codes or standards
| Schedule | See under Schedules
| Daylighting Controls | Requirements in codes or standards |  |  | Applicable codes or standards
| Occupancy Sensors | Requirements in codes or standards |  |  | Applicable codes or standards
Plug load
| Average power density (W/ft2) | See Zone Summary
| Schedule | See under Schedules
Occupancy
| Average people | See under Zone Summary
| Schedule | See under Schedules
Misc.
Elevator
| Quantity |  | 8 |  | Reference: DOE Commercial Reference Building Models of the National Building Stock
| Motor type |  | Traction
| Peak Motor Power (watts/elevator) |  | 20370
| Heat Gain to Building |  | Exterior
| Peak Fan/lights Power (watts/elevator) |  | 161.9 |  | 90.1 Mechanical Subcommittee, Elevator Working Group
| Motor and fan/lights Schedules |  | See under Schedules |  | Reference: DOE Commercial Reference Building Models of the National Building Stock
Exterior Lighting
| Peak Power (W) | Based on design assumptions for façade, parking lot, entrance, etc. and requirements in codes or standards |  |  | Applicable codes or standards
| Schedule | See under Schedules and control requirements in codes or standards |  |  | Applicable codes or standards
References
ASHRAE 2013. ANSI/ASHRAE Standard 169-2013. Climatic Data for Building Design Standards. American Society of Heating, Refrigerating, and Air-Conditioning Engineers, Atlanta, Georgia. Relevant information available as Annex 1 in ASHRAE 2016
McGraw-Hill Companies, Inc. 2001. Time-Saver Standards for Building Types. New York, NY.
LBNL (1991). Huang, Joe, Akbari, H., Rainer, L. and Ritschard, R. 481 Prototypical Commercial Buildings for 20 Urban Market Areas, prepared for the Gas Research Institute, Chicago IL, also LBL-29798, Berkeley CA.
PNNL's CBECS Study. 2007. Analysis of Building Envelope Construction in 2003 CBECS Buildings. Dave Winiarski, Mark Halverson, and Wei Jiang. Pacific Northwest National Laboratory. March 2007.
PNNL's CBECS Study. 2006. Review of Pre- and Post-1980 Buildings in CBECS – HVAC Equipment. Dave Winiarski, Wei Jiang and Mark Halverson. Pacific Northwest National Laboratory. December 2006.
Gowri K, DW Winiarski, and RE Jarnagin. 2009. Infiltration modeling guidelines for commercial building energy analysis . PNNL-18898, Pacific Northwest National Laboratory, Richland, WA. http://www.pnl.gov/main/publications/external/technical_reports/PNNL-18898.pdf
Goel S, M Rosenberg, R Athalye, Y Xie, W Wang, R Hart, J Zhang, V Mendon. 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models. PNNL-23269, Pacific Northwest National Laboratory, Richland, Washington. http://www.pnnl.gov/main/publications/external/technical_reports/PNNL-23269.pdf
AIA. 2001. AIA Guidelines for Design and Construction of Hospital and Health Care Facilities: 2001 Edition. American Institute of Architects, Washington, D.C..

## Zone Summary
Zone Summary
Zone | Area (ft²) | Conditioned (Y/N) | Volume (ft³) | Multipliers | Gross Wall Area (ft²) | Window Glass Area (ft²) | Lighting (W/ft²)2 | People (ft²/person) | Number of People | Plug and Process (W/ft²)
BASEMENT | 40235.406 | No | 321832.0019 | 1 | 0 | 0 | 1 | 400 | 100.5885 | 0.75
First Floor
ER_EXAM1_MULT4_FLR_1 | 299.8812 | Yes | 4197.8072 | 4 | 279.9752 | 0 | 2.6998 | 50 | 5.9976 | 1.5
ER_TRAUMA1_FLR_1 | 299.8812 | Yes | 4197.8072 | 1 | 489.9028 | 0 | 2.6998 | 50 | 5.9976 | 4
ER_EXAM3_MULT4_FLR_1 | 299.8812 | Yes | 4197.8072 | 4 | 209.9276 | 0 | 2.6998 | 50 | 5.9976 | 1.5
ER_TRAUMA2_FLR_1 | 299.8812 | Yes | 4197.8072 | 1 | 489.9028 | 0 | 2.6998 | 50 | 5.9976 | 4
ER_TRIAGE_MULT4_FLR_1 | 299.8812 | Yes | 4197.8072 | 4 | 279.9752 | 0 | 2.6998 | 50 | 5.9976 | 2
OFFICE1_MULT4_FLR_1 | 149.9944 | Yes | 2099.6093 | 5 | 139.9876 | 31.8496 | 1 | 142.8571 | 1.05 | 1.1
LOBBY_RECORDS_FLR_1 | 15868.9556 | Yes | 222132.3168 | 1 | 4409.2328 | 673.8988 | 1.27 | 750 | 21.1586 | 0.1
CORRIDOR_FLR_1 | 6122.7628 | Yes | 85706.0534 | 1 | 979.9132 | 0 | 1 | 1000 | 6.1228 | 0
ER_NURSESTN_LOBBY_FLR_1 | 13295.1636 | Yes | 186104.7849 | 1 | 1189.8408 | 327.3192 | 1.12 | 750 | 17.7269 | 1.36
2nd Floor
OR1_FLR_2 | 599.7624 | Yes | 8395.2615 | 1 | 699.938 | 0 | 2.1998 | 200 | 2.9988 | 4
OR2_MULT5_FLR_2 | 599.7624 | Yes | 8395.2615 | 5 | 279.9752 | 0 | 2.1998 | 200 | 2.9988 | 4
OR3_FLR_2 | 599.7624 | Yes | 8395.2615 | 1 | 419.9628 | 0 | 2.1998 | 200 | 2.9988 | 4
OR4_FLR_2 | 2399.1572 | Yes | 33583.1632 | 1 | 0 | 0 | 2.1998 | 200 | 11.9958 | 4
IC_PATROOM1_MULT5_FLR_2 | 224.884 | Yes | 3148.0025 | 5 | 209.9276 | 52.8316 | 0.80019 | 200 | 1.1244 | 3
IC_PATROOM2_FLR_2 | 299.8812 | Yes | 4197.8072 | 1 | 489.9028 | 123.0944 | 0.80019 | 200 | 1.4994 | 3
IC_PATROOM3_MULT6_FLR_2 | 224.884 | Yes | 3148.0025 | 6 | 209.9276 | 52.8316 | 0.80019 | 200 | 1.1244 | 3
ICU_FLR_2 | 6649.2496 | Yes | 93075.5058 | 1 | 2309.9568 | 269.3228 | 0.80019 | 200 | 33.2462 | 3
ICU_NURSESTN_LOBBY_FLR_2 | 7195.9652 | Yes | 100728.6701 | 1 | 0 | 0 | 1 | 750 | 9.5946 | 2
CORRIDOR_FLR_2 | 6122.7628 | Yes | 85706.0534 | 1 | 979.9132 | 0 | 1 | 1000 | 6.1228 | 0
OR_NURSESTN_LOBBY_FLR_2 | 10896.0064 | Yes | 152521.2688 | 1 | 1959.8264 | 384.7776 | 1.18 | 750 | 14.528 | 1.04
3rd Floor
PATROOM1_MULT10_FLR_3 | 224.884 | Yes | 3148.0025 | 10 | 209.9276 | 52.8316 | 0.69981 | 200 | 1.1244 | 2
PATROOM2_FLR_3 | 374.8784 | Yes | 5247.6119 | 1 | 559.9504 | 140.7408 | 0.69981 | 200 | 1.8744 | 2
PATROOM3_MULT10_FLR_3 | 217.4596 | Yes | 3043.9042 | 10 | 203.0412 | 51.0024 | 0.69981 | 200 | 1.0873 | 2
PATROOM4_FLR_3 | 374.8784 | Yes | 5247.6119 | 1 | 559.9504 | 140.7408 | 0.69981 | 200 | 1.8744 | 2
PATROOM5_MULT10_FLR_3 | 224.884 | Yes | 3148.0025 | 10 | 209.9276 | 52.8316 | 0.69981 | 200 | 1.1244 | 2
PHYSTHERAPY_FLR_3 | 5248.0824 | Yes | 73462.3315 | 1 | 0 | 0 | 0.89963 | 200 | 26.2404 | 1.5
PATROOM6_FLR_3 | 299.8812 | Yes | 4197.8072 | 1 | 489.9028 | 123.0944 | 0.69981 | 200 | 1.4994 | 2
PATROOM7_MULT10_FLR_3 | 217.4596 | Yes | 3043.9042 | 10 | 203.0412 | 51.0024 | 0.69981 | 200 | 1.0873 | 2
PATROOM8_FLR_3 | 299.8812 | Yes | 4197.8072 | 1 | 489.9028 | 123.0944 | 0.69981 | 200 | 1.4994 | 2
NURSESTN_LOBBY_FLR_3 | 9746.408 | Yes | 136430.4979 | 1 | 419.9628 | 0 | 1.18 | 750 | 12.9952 | 1.04
LAB_FLR_3 | 2848.9252 | Yes | 39854.8199 | 1 | 0 | 0 | 1.3996 | 200 | 14.2446 | 4
CORRIDOR_SE_FLR_3 | 6097.7996 | Yes | 85356.3538 | 1 | 489.9028 | 0 | 1 | 1000 | 6.0978 | 0
CORRIDOR_NW_FLR_3 | 6097.7996 | Yes | 85356.3538 | 1 | 907.3908 | 0 | 1 | 1000 | 6.0978 | 0
4th Floor
PATROOM1_MULT10_FLR_4 | 224.884 | Yes | 3148.0025 | 10 | 209.9276 | 52.8316 | 0.69981 | 200 | 1.1244 | 2
PATROOM2_FLR_4 | 374.8784 | Yes | 5247.6119 | 1 | 559.9504 | 140.7408 | 0.69981 | 200 | 1.8744 | 2
PATROOM3_MULT10_FLR_4 | 217.4596 | Yes | 3043.9042 | 10 | 203.0412 | 51.0024 | 0.69981 | 200 | 1.0873 | 2
PATROOM4_FLR_4 | 374.8784 | Yes | 5247.6119 | 1 | 559.9504 | 140.7408 | 0.69981 | 200 | 1.8744 | 2
PATROOM5_MULT10_FLR_4 | 224.884 | Yes | 3148.0025 | 10 | 209.9276 | 52.8316 | 0.69981 | 200 | 1.1244 | 2
RADIOLOGY_FLR_4 | 5248.0824 | Yes | 73462.3315 | 1 | 0 | 0 | 0.39963 | 200 | 26.2404 | 10
PATROOM6_FLR_4 | 299.8812 | Yes | 4197.8072 | 1 | 489.9028 | 123.0944 | 0.69981 | 200 | 1.4994 | 2
PATROOM7_MULT10_FLR_4 | 217.4596 | Yes | 3043.9042 | 10 | 203.0412 | 51.0024 | 0.69981 | 200 | 1.0873 | 2
PATROOM8_FLR_4 | 299.8812 | Yes | 4197.8072 | 1 | 489.9028 | 123.0944 | 0.69981 | 200 | 1.4994 | 2
NURSESTN_LOBBY_FLR_4 | 9746.408 | Yes | 136429.4393 | 1 | 419.9628 | 0 | 1.18 | 750 | 12.9952 | 1.04
LAB_FLR_4 | 2848.9252 | Yes | 39854.8199 | 1 | 0 | 0 | 1.3996 | 200 | 14.2446 | 4
CORRIDOR_SE_FLR_4 | 6097.7996 | Yes | 85356.3538 | 1 | 489.9028 | 0 | 1 | 1000 | 6.0978 | 0
CORRIDOR_NW_FLR_4 | 6097.7996 | Yes | 85356.3538 | 1 | 907.3908 | 0 | 1 | 1000 | 6.0978 | 0
5th Floor
DINING_FLR_5 | 7497.2452 | Yes | 104946.5912 | 1 | 2449.7292 | 384.7776 | 0.89963 | 100 | 74.9725 | 1
NURSESTN_LOBBY_FLR_5 | 11195.8876 | Yes | 156720.1346 | 1 | 1119.9008 | 0 | 1.18 | 750 | 14.9279 | 1.04
KITCHEN_FLR_5 | 9996.3628 | Yes | 139928.2001 | 1 | 2799.752 | 0 | 1.1998 | 200 | 49.9818 | 22.63
OFFICE1_FLR_5 | 749.972 | Yes | 10498.0467 | 1 | 769.9856 | 193.4648 | 1 | 142.8571 | 5.2498 | 1
OFFICE2_MULT5_FLR_5 | 749.7568 | Yes | 10494.8708 | 5 | 349.9152 | 87.9092 | 1 | 142.8571 | 5.2483 | 1
OFFICE3_FLR_5 | 749.7568 | Yes | 10494.8708 | 1 | 769.878 | 193.4648 | 1 | 142.8571 | 5.2483 | 1
OFFICE4_MULT6_FLR_5 | 149.9944 | Yes | 2099.6093 | 6 | 139.9876 | 31.8496 | 1 | 142.8571 | 1.05 | 1
CORRIDOR_FLR_5 | 5398.0768 | Yes | 75561.9408 | 1 | 839.9256 | 0 | 1 | 1000 | 5.3981 | 0
TOTAL1 | 241412.5436 |  | 3137849.2266 |  | 57598.1724 | 9129.86 |  |  | 766.7956
AREA WEIGHTED AVERAGE | [6 empty] | 1.0839 | 542.8608 |  | 2.2168
1. Only volume, and gross wall area include unconditioned space.
2. Listed lighting power density is based on applicable requirements in ASHRAE Standard 90.1-2004. The actual inputs for the models are based on appliable codes and standards

## Outdoor&Supply Air
Minimum Outdoor Ventilation Air Requirements
[7 empty] | Total OSA Ventilation (cfm/zone) | [5 empty] | Total OSA Ventilation (cfm/ft2) |  |  | Minimum Total Supply Air Rate (cfm/zone) | Minimum Total Supply Air Rate (cfm/ft2)
[7 empty] | 90.1-2004 baseline model will use the maximum between these two standards |  | 90.1-2007 model will use the maximum between these two standards |  | 90.1-2010 model will use the maximum between these two standards
Zone | Area (ft2) | Multipliers | Assumed Space Type by ASHRAE Standard 62 | Assumed Space Type by AIA Guidelines | Occupant Density (ft2/person) | Total Occupants | ASHRAE 62-1999 | AIA Guide 2001 | ASHRAE 62.1-2004 | AIA Guide 2006 | ASHRAE 62.1-2007 | AIA Guide 2006 | 90.1-2004 | 90.1-2007 | 90.1-2010 | AIA Guide 2001 and 2006 | 90.1-2004, 2007, and 2010 AIA Guide 2001 and 2006
BASEMENT | 40235.406 | 1 | Office space |  | 400 | 100.5885 | 2011.7703 | 2011.7703 | 2917.0669 | 2917.0669 | 2917.0669 | 2917.0669 | 0.05 | 0.0725 | 0.0725 | NA | NA
First Floor
ER_EXAM1_MULT4_FLR_1 | 299.8812 | 4 | Medical procedure | ER Waiting Room | 50 | 5.9976 | 89.9644 | 139.9269 | 89.9644 | 139.9269 | 89.9644 | 139.9269 | 0.46661 | 0.46661 | 0.46661 | 839.5614 | 2.7996
ER_TRAUMA1_FLR_1 | 299.8812 | 1 | Medical procedure | ER Waiting Room | 50 | 5.9976 | 89.9644 | 139.9269 | 89.9644 | 139.9269 | 89.9644 | 139.9269 | 0.46661 | 0.46661 | 0.46661 | 839.5614 | 2.7996
ER_EXAM3_MULT4_FLR_1 | 299.8812 | 4 | Medical procedure | ER Waiting Room | 50 | 5.9976 | 89.9644 | 139.9269 | 89.9644 | 139.9269 | 89.9644 | 139.9269 | 0.46661 | 0.46661 | 0.46661 | 839.5614 | 2.7996
ER_TRAUMA2_FLR_1 | 299.8812 | 1 | Medical procedure | ER Waiting Room | 50 | 5.9976 | 89.9644 | 139.9269 | 89.9644 | 139.9269 | 89.9644 | 139.9269 | 0.46661 | 0.46661 | 0.46661 | 839.5614 | 2.7996
ER_TRIAGE_MULT4_FLR_1 | 299.8812 | 4 | Medical procedure | ER Waiting Room | 50 | 5.9976 | 89.9644 | 139.9269 | 89.9644 | 139.9269 | 89.9644 | 139.9269 | 0.46661 | 0.46661 | 0.46661 | 839.5614 | 2.7996
OFFICE1_MULT4_FLR_1 | 149.9944 | 5 | Office space |  | 142.8571 | 1.05 | 20.9992 | 20.9992 | 14.2495 | 14.2495 | 14.2495 | 14.2495 | 0.14 | 0.095 | 0.095 | NA | NA
LOBBY_RECORDS_FLR_1 | 15868.9556 | 1 | Lobbies |  | 750 | 21.1586 | 423.1721 | 423.1721 | 1057.9304 | 1057.9304 | 1057.9304 | 1057.9304 | 0.026667 | 0.066667 | 0.066667 | NA | NA
CORRIDOR_FLR_1 | 6122.7628 | 1 | Corridors (public spaces) |  | 1000 | 6.1228 | 306.1381 | 306.1381 | 367.3658 | 367.3658 | 367.3658 | 367.3658 | 0.05 | 0.06 | 0.06 | NA | NA
ER_NURSESTN_LOBBY_FLR_1 | 13295.1636 | 1 | Reception areas |  | 750 | 17.7269 | 265.9033 | 265.9033 | 886.3442 | 886.3442 | 886.3442 | 886.3442 | 0.02 | 0.066667 | 0.066667 | NA | NA
2nd Floor
OR1_FLR_2 | 599.7624 | 1 | Operating rooms | Operating/Surgical Cystoscopic Rooms | 200 | 2.9988 | 89.9644 | 419.7631 | 89.9644 | 419.7631 | 89.9644 | 419.7631 | 0.69988 | 0.69988 | 0.69988 | 2098.8154 | 3.4994
OR2_MULT5_FLR_2 | 599.7624 | 5 | Operating rooms | Operating/Surgical Cystoscopic Rooms | 200 | 2.9988 | 89.9644 | 419.7631 | 89.9644 | 419.7631 | 89.9644 | 419.7631 | 0.69988 | 0.69988 | 0.69988 | 2098.8154 | 3.4994
OR3_FLR_2 | 599.7624 | 1 | Operating rooms | Operating/Surgical Cystoscopic Rooms | 200 | 2.9988 | 89.9644 | 419.7631 | 89.9644 | 419.7631 | 89.9644 | 419.7631 | 0.69988 | 0.69988 | 0.69988 | 2098.8154 | 3.4994
OR4_FLR_2 | 2399.1572 | 1 | Operating rooms | Operating/Surgical Cystoscopic Rooms | 200 | 11.9958 | 359.8736 | 1679.1582 | 359.8736 | 1679.1582 | 359.8736 | 1679.1582 | 0.6999 | 0.6999 | 0.6999 | 8395.7908 | 3.4995
IC_PATROOM1_MULT5_FLR_2 | 224.884 | 5 | Recovery and ICU | Critical and Intensive Care | 200 | 1.1244 | 16.8663 | 104.9334 | 16.8663 | 104.9334 | 16.8663 | 104.9334 | 0.46661 | 0.46661 | 0.46661 | 314.8003 | 1.3998
IC_PATROOM2_FLR_2 | 299.8812 | 1 | Recovery and ICU | Critical and Intensive Care | 200 | 1.4994 | 22.4911 | 139.9269 | 22.4911 | 139.9269 | 22.4911 | 139.9269 | 0.46661 | 0.46661 | 0.46661 | 419.7807 | 1.3998
IC_PATROOM3_MULT6_FLR_2 | 224.884 | 6 | Recovery and ICU | Critical and Intensive Care | 200 | 1.1244 | 16.8663 | 104.9334 | 16.8663 | 104.9334 | 16.8663 | 104.9334 | 0.46661 | 0.46661 | 0.46661 | 314.8003 | 1.3998
ICU_FLR_2 | 6649.2496 | 1 | Recovery and ICU | Critical and Intensive Care | 200 | 33.2462 | 498.6937 | 3102.5169 | 498.6937 | 3102.5169 | 498.6937 | 3102.5169 | 0.4666 | 0.4666 | 0.4666 | 9307.5506 | 1.3998
ICU_NURSESTN_LOBBY_FLR_2 | 7195.9652 | 1 | Reception areas |  | 750 | 9.5946 | 143.9193 | 143.9193 | 479.731 | 479.731 | 479.731 | 479.731 | 0.02 | 0.066667 | 0.066667 | NA | NA
CORRIDOR_FLR_2 | 6122.7628 | 1 | Corridors (public spaces) |  | 1000 | 6.1228 | 306.1381 | 306.1381 | 367.3658 | 367.3658 | 367.3658 | 367.3658 | 0.05 | 0.06 | 0.06 | NA | NA
OR_NURSESTN_LOBBY_FLR_2 | 10896.0064 | 1 | Reception areas |  | 750 | 14.528 | 217.9201 | 217.9201 | 726.4004 | 726.4004 | 726.4004 | 726.4004 | 0.02 | 0.066667 | 0.066667 | NA | NA
3rd Floor
PATROOM1_MULT10_FLR_3 | 224.884 | 10 | Patient rooms | Patient Room | 200 | 1.1244 | 28.1105 | 104.9334 | 28.1105 | 104.9334 | 28.1105 | 104.9334 | 0.46661 | 0.46661 | 0.46661 | 314.8003 | 1.3998
PATROOM2_FLR_3 | 374.8784 | 1 | Patient rooms | Patient Room | 200 | 1.8744 | 46.8598 | 174.9204 | 46.8598 | 174.9204 | 46.8598 | 174.9204 | 0.46661 | 0.46661 | 0.46661 | 524.7612 | 1.3998
PATROOM3_MULT10_FLR_3 | 217.4596 | 10 | Patient rooms | Patient Room | 200 | 1.0873 | 27.1824 | 101.4635 | 27.1824 | 101.4635 | 27.1824 | 101.4635 | 0.46659 | 0.46659 | 0.46659 | 304.3904 | 1.3998
PATROOM4_FLR_3 | 374.8784 | 1 | Patient rooms | Patient Room | 200 | 1.8744 | 46.8598 | 174.9204 | 46.8598 | 174.9204 | 46.8598 | 174.9204 | 0.46661 | 0.46661 | 0.46661 | 524.7612 | 1.3998
PATROOM5_MULT10_FLR_3 | 224.884 | 10 | Patient rooms | Patient Room | 200 | 1.1244 | 28.1105 | 104.9334 | 28.1105 | 104.9334 | 28.1105 | 104.9334 | 0.46661 | 0.46661 | 0.46661 | 314.8003 | 1.3998
PHYSTHERAPY_FLR_3 | 5248.0824 | 1 | Physical therapy |  | 200 | 26.2404 | 393.6062 | 393.6062 | 393.6062 | 393.6062 | 393.6062 | 393.6062 | 0.075 | 0.075 | 0.075 | NA | NA
PATROOM6_FLR_3 | 299.8812 | 1 | Patient rooms | Patient Room | 200 | 1.4994 | 37.4851 | 139.9269 | 37.4851 | 139.9269 | 37.4851 | 139.9269 | 0.46661 | 0.46661 | 0.46661 | 419.7807 | 1.3998
PATROOM7_MULT10_FLR_3 | 217.4596 | 10 | Patient rooms | Patient Room | 200 | 1.0873 | 27.1824 | 101.4635 | 27.1824 | 101.4635 | 27.1824 | 101.4635 | 0.46659 | 0.46659 | 0.46659 | 304.3904 | 1.3998
PATROOM8_FLR_3 | 299.8812 | 1 | Patient rooms | Patient Room | 200 | 1.4994 | 37.4851 | 139.9269 | 37.4851 | 139.9269 | 37.4851 | 139.9269 | 0.46661 | 0.46661 | 0.46661 | 419.7807 | 1.3998
NURSESTN_LOBBY_FLR_3 | 9746.408 | 1 | Lobbies |  | 750 | 12.9952 | 259.9042 | 259.9042 | 649.7605 | 649.7605 | 649.7605 | 649.7605 | 0.026667 | 0.066667 | 0.066667 | NA | NA
LAB_FLR_3 | 2848.9252 | 1 | Science laboratories |  | 200 | 14.2446 | 284.8925 | 284.8925 | 655.2528 | 655.2528 | 655.2528 | 655.2528 | 0.1 | 0.23 | 0.23 | NA | NA
CORRIDOR_SE_FLR_3 | 6097.7996 | 1 | Corridors (public spaces) |  | 1000 | 6.0978 | 304.89 | 304.89 | 365.868 | 365.868 | 365.868 | 365.868 | 0.05 | 0.06 | 0.06 | NA | NA
CORRIDOR_NW_FLR_3 | 6097.7996 | 1 | Corridors (public spaces) |  | 1000 | 6.0978 | 304.89 | 304.89 | 365.868 | 365.868 | 365.868 | 365.868 | 0.05 | 0.06 | 0.06 | NA | NA
4th Floor |  |  |  |  | 0
PATROOM1_MULT10_FLR_4 | 224.884 | 10 | Patient rooms | Patient Room | 200 | 1.1244 | 28.1105 | 104.9334 | 28.1105 | 104.9334 | 28.1105 | 104.9334 | 0.46661 | 0.46661 | 0.46661 | 314.8003 | 1.3998
PATROOM2_FLR_4 | 374.8784 | 1 | Patient rooms | Patient Room | 200 | 1.8744 | 46.8598 | 174.9204 | 46.8598 | 174.9204 | 46.8598 | 174.9204 | 0.46661 | 0.46661 | 0.46661 | 524.7612 | 1.3998
PATROOM3_MULT10_FLR_4 | 217.4596 | 10 | Patient rooms | Patient Room | 200 | 1.0873 | 27.1824 | 101.4635 | 27.1824 | 101.4635 | 27.1824 | 101.4635 | 0.46659 | 0.46659 | 0.46659 | 304.3904 | 1.3998
PATROOM4_FLR_4 | 374.8784 | 1 | Patient rooms | Patient Room | 200 | 1.8744 | 46.8598 | 174.9204 | 46.8598 | 174.9204 | 46.8598 | 174.9204 | 0.46661 | 0.46661 | 0.46661 | 524.7612 | 1.3998
PATROOM5_MULT10_FLR_4 | 224.884 | 10 | Patient rooms | Patient Room | 200 | 1.1244 | 28.1105 | 104.9334 | 28.1105 | 104.9334 | 28.1105 | 104.9334 | 0.46661 | 0.46661 | 0.46661 | 314.8003 | 1.3998
RADIOLOGY_FLR_4 | 5248.0824 | 1 | Medical procedure |  | 200 | 26.2404 | 393.6062 | 393.6062 | 393.6062 | 393.6062 | 393.6062 | 393.6062 | 0.075 | 0.075 | 0.075 | NA | NA
PATROOM6_FLR_4 | 299.8812 | 1 | Patient rooms | Patient Room | 200 | 1.4994 | 37.4851 | 139.9269 | 37.4851 | 139.9269 | 37.4851 | 139.9269 | 0.46661 | 0.46661 | 0.46661 | 419.7807 | 1.3998
PATROOM7_MULT10_FLR_4 | 217.4596 | 10 | Patient rooms | Patient Room | 200 | 1.0873 | 27.1824 | 101.4635 | 27.1824 | 101.4635 | 27.1824 | 101.4635 | 0.46659 | 0.46659 | 0.46659 | 304.3904 | 1.3998
PATROOM8_FLR_4 | 299.8812 | 1 | Patient rooms | Patient Room | 200 | 1.4994 | 37.4851 | 139.9269 | 37.4851 | 139.9269 | 37.4851 | 139.9269 | 0.46661 | 0.46661 | 0.46661 | 419.7807 | 1.3998
NURSESTN_LOBBY_FLR_4 | 9746.408 | 1 | Lobbies |  | 750 | 12.9952 | 259.9042 | 259.9042 | 649.7605 | 649.7605 | 649.7605 | 649.7605 | 0.026667 | 0.066667 | 0.066667 | NA | NA
LAB_FLR_4 | 2848.9252 | 1 | Science laboratories |  | 200 | 14.2446 | 284.8925 | 284.8925 | 655.2528 | 655.2528 | 655.2528 | 655.2528 | 0.1 | 0.23 | 0.23 | NA | NA
CORRIDOR_SE_FLR_4 | 6097.7996 | 1 | Corridors (public spaces) |  | 1000 | 6.0978 | 304.89 | 304.89 | 365.868 | 365.868 | 365.868 | 365.868 | 0.05 | 0.06 | 0.06 | NA | NA
CORRIDOR_NW_FLR_4 | 6097.7996 | 1 | Corridors (public spaces) |  | 1000 | 6.0978 | 304.89 | 304.89 | 365.868 | 365.868 | 365.868 | 365.868 | 0.05 | 0.06 | 0.06 | NA | NA
5th Floor
DINING_FLR_5 | 7497.2452 | 1 | Cafeteria / fast food dining |  | 100 | 74.9725 | 1499.449 | 1499.449 | 1911.7975 | 1911.7975 | 1911.7975 | 1911.7975 | 0.2 | 0.255 | 0.255 | NA | NA
NURSESTN_LOBBY_FLR_5 | 11195.8876 | 1 | Reception areas |  | 750 | 14.9279 | 223.9178 | 223.9178 | 746.3925 | 746.3925 | 746.3925 | 746.3925 | 0.02 | 0.066667 | 0.066667 | NA | NA
KITCHEN_FLR_5 | 9996.3628 | 1 | Kitchen |  | 200 | 49.9818 | 749.7272 | 749.7272 | 6997.454 | 6997.454 | 6997.454 | 6997.454 | 0.075 | 0.7 | 0.7 | NA | NA
OFFICE1_FLR_5 | 749.972 | 1 | Office space |  | 142.8571 | 5.2498 | 104.9961 | 104.9961 | 71.2473 | 71.2473 | 71.2473 | 71.2473 | 0.14 | 0.095 | 0.095 | NA | NA
OFFICE2_MULT5_FLR_5 | 749.7568 | 5 | Office space |  | 142.8571 | 5.2483 | 104.966 | 104.966 | 71.2269 | 71.2269 | 71.2269 | 71.2269 | 0.14 | 0.095 | 0.095 | NA | NA
OFFICE3_FLR_5 | 749.7568 | 1 | Office space |  | 142.8571 | 5.2483 | 104.966 | 104.966 | 71.2269 | 71.2269 | 71.2269 | 71.2269 | 0.14 | 0.095 | 0.095 | NA | NA
OFFICE4_MULT6_FLR_5 | 149.9944 | 6 | Office space |  | 142.8571 | 1.05 | 20.9992 | 20.9992 | 14.2495 | 14.2495 | 14.2495 | 14.2495 | 0.14 | 0.095 | 0.095 | NA | NA
CORRIDOR_FLR_5 | 5398.0768 | 1 | Corridors (public spaces) |  | 1000 | 5.3981 | 269.9038 | 269.9038 | 323.8846 | 323.8846 | 323.8846 | 323.8846 | 0.05 | 0.06 | 0.06 | NA | NA
TOTAL | 241412.5436 | [5 empty] | 15985.0452 | 30968.5608 | 27802.734 | 42786.2495 | 27802.734 | 42786.2495 | 62.9632 | 63.4924 | 63.4924 | 76577.2872 | 208.5704
Note: The ventilation requirements for other codes or standards are based on their reference ASHRAE Standard 62.1, International Mechanical Code, or AIA Guide

## Schedules
Schedule | Type | Through | Day of Week | 1 am | 2 am | 3 am | 4 am | 5 am | 6 am | 7 am | 8 am | 9 am | 10 am | 11 am | Noon | 1 pm | 2 pm | 3 pm | 4 pm | 5 pm | 6 pm | 7 pm | 8 pm | 9 pm | 10 pm | 11 pm | 12 pm
Internal Loads Schedules
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Office, Lobby, Clinic, OR |  |  | Sat, WinterDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
BLDG_LIGHT_EXTD_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
ER, Patient Rm, ICU, Nurse Station, Dinning, Kitchen |  |  | Sat, WinterDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4
|  |  | Sat, WinterDesign | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
BLDG_EQUIP_EXTD_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4
|  |  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0 | 0
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_EXTD_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sat, WinterDesign | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
BLDG_ELEVATORS | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2
|  |  | Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
|  |  | Sun | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesign | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
ELEV_LIGHT_FAN_SCH_24_7 | Fraction | Through 12/31 | WD | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Service Water Heater Load Schedule
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01
|  |  | Sat, WinterDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
|  |  | Sun, Hol, Other | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Laundry_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_SWH_EXTD_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.301 | 0.3 | 0.5 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3
|  |  | Sat, WinterDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Infiltration Schedule
INFIL_SCH_PNNL | fraction | Through 12/31 | WD, SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  | Sat, WinterDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  | Sun, Hol, Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HVAC Schedules
HVACOperationSchd | on/off | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
(fan schedule)
HTGSETP_SCH | Temperature | Through 12/31 | All | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
CLGSETP_SCH | Temperature | Through 12/31 | All | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Heat-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
HTGSETP_SCH | Temperature | Through 12/31 | All | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8
CLGSETP_SCH | Temperature | Through 12/31 | All | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140
Heat-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8
ReheatCoilAvailSched | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
CoolingCoilAvailSched | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
| (%) |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
MinOA_Sched | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
VAV_ER_OAminOAFracSchedule | Fraction | Through 12/31 | All | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
VAV_OR_OAminOAFracSchedule | Fraction | Through 12/31 | All | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
VAV_ICU_OAminOAFracSchedule | Fraction | Through 12/31 | All | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
VAV_PATRMS_OAminOAFracSchedule | Fraction | Through 12/31 | All | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
VAV_LABS_OAminOAFracSchedule | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen_SAT_SCH | Temperature | Through 12/31 | All | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
VAV_SAT_SCH | Temperature | Through 12/31 | All | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
MinRelHumSetSch | Humidity | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Notes: | The schedules are also subject to changes in different models based on applicable code requrirements triggered by cllimate zone, system capacity, control type, or other criteria.