## Building Description
Prototype Building Modeling Specifications
Pacific Northwest National Laboratory, updated on October 18, 2018
| Item | Descriptions |  |  | Data Source
Program
| Vintage | NEW CONSTRUCTION
| Location (Representing 8 Climate Zones) | Zone 1A: Honolulu, Hawaii (very hot, humid) Zone 1B: New Delhi, India (very hot, dry) Zone 2A: Tampa, Florida (hot, humid) Zone 2B: Tucson, Arizona (hot, dry) Zone 3A: Atlanta, Georgia (warm, humid) Zone 3B: El Paso, Texas (warm, dry) Zone 3C: San Diego, California (warm, marine) | Zone 4A: New York, New York (mixed, humid) Zone 4B: Albuquerque, New Mexico (mixed, dry) Zone 4C: Seattle, Washington (mixed, marine) Zone 5A: Buffalo, NY (cool, humid) Zone 5B: Denver, Colorado (cool, dry) Zone 5C: Port Angeles, Washington (cool, marine) | Zone 6A: Rochester, Minnesota (cold, humid) Zone 6B: Great Falls, Montana (cold, dry) Zone 7: International Falls, Minnesota (very cold) Zone 8: Fairbanks, Alaska (subarctic | Selection of representative climates based on ASHRAE Standard 169-2013
| Available fuel types | Gas, electricity
| Building Type (Principal Building Function) | Lodging
| Building Prototype | Large Hotel
Form
| Total Floor Area (sq feet) | 122132
Building shape
| Aspect Ratio | Ground floor: 3.79 (284 ft x 75 ft) All other floors: 5.07 (284 ft x 56 ft)
| Number of Floors | 6 above-ground floors plus one basement (284 ft x 75 ft)
| Window Fraction (Window-to-Wall Ratio) | South: 36.7%, East: 24.5%, North: 26.0%, West: 24.5% Total: 30.2%
| Window Locations | For standard guest room, one per guest room (9.9' x 4')
| Shading Geometry | None
| Azimuth | Non-directional
Thermal Zoning
Basement: conditioned single zone; Ground Floor: 7 zones including retails, lobby, cafe, laundry, storage and mechanical rooms; 2nd to 5th Floor (guest-floor): 7 zones per floor, including guest rooms and corridor. Each floor has 42 guest rooms; 6th Floor: 7 zones including guest rooms, banquet room, dining, kitchen and corridor. Total 179 guest rooms, accounting for 41% of total floor area.
| Floor to floor height (feet) | Basement: 8 ft Ground floor: 13 ft 2nd - 6th floors: 10 ft
| Floor to ceiling height (feet) | Same as above
| Glazing sill height (feet) | 6 in. in ground floor, 3.6 ft. in upper floors
Architecture
Exterior walls
| Construction | Mass Wall: 8 in. CMU, wall insulation and 0.5 in. gypsum board |  |  | 2003 CBECS Database (Based on PNNL's Study)
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; Walls, Above-Grade, Steel-Framed for ground floor Residential: Walls, Above-Grade, Steel-Framed for remaining floors |  |  | Applicable codes or standards
| Dimensions | Based on floor area and aspect ratio
| Tilts and orientations | Vertical
Roof
| Construction | Insulation entirely above Deck (Single-ply roof membrane, steel deck with rigid insulation) |  |  | 2003 CBECS Database (Based on PNNL's Study)
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; Roofs, Insulation entirely above deck |  |  | Applicable codes or standards
| Dimensions | Based on floor area and aspect ratio
| Tilts and orientations | Horizontal
Window
| Dimensions | Based on window fraction, location, glazing sill height, floor area and aspect ratio
| Glass-Type and frame | Hypothetical window with a weighted U-factor and SHGC
| U-factor (Btu / h * ft2 * °F) | Requirements in codes or standards Nonresidential for ground floor and residential for upper floors |  |  | Applicable codes or standards
SHGC (all)
| Visible transmittance | Same as above requirements
| Operable area | 22% |  |  | ASHRAE SSPC 90.1 (Fenestration Market Survey Data)
Skylight
| Dimensions | Not modeled
| Glass-Type and frame | NA
U-factor (Btu / h * ft2 * °F)
SHGC (all)
Visible transmittance
Foundation
| Foundation Type | Basement (conditioned)
| Construction | 8" heavy-weight Concrete with carpet for all walls and slabs in the model
| Thermal properties for basement walls | Requirements in codes or standards |  |  | Applicable codes or standards
| Dimensions | Based on floor area and aspect ratio
Interior Partitions
| Construction | 1 in. gypsum board
| Dimensions | Based on floor plan and floor-to-floor height
| Internal Mass | 6 inches standard wood (16.6 lb/ft²)
Air Barrier System
| Infiltration | Peak: 0.2016 cfm/sf of above grade exterior wall surface area, adjusted by wind (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) |  |  | Reference: PNNL-18898. Infiltration Modeling Guidelines for Commercial Building Energy Analysis. Modeled peak infiltration rate may be different for different codes or standards because of their continuous air barrier requirements.
HVAC
System Type
| Heating type | One gas-fired boiler
| Cooling type | One air-cooled chiller
| Distribution and terminal units | Public spaces on ground floor and top floor: VAV with hot water reheating coils; Guest rooms: dedicated outside air system + four-pipe fan-coil units. |  |  | 2003 CBECS Database (Based on PNNL's Study)
HVAC Sizing
| Air Conditioning | Autosized to design day
| Heating | Autosized to design day
HVAC Efficiency
| Air Conditioning | Requirements in codes or standards for chiller and boiler. |  |  | Applicable codes or standards
Heating
HVAC Control
| Thermostat Setpoint | Guest Rooms: 70°F Cooling/ 70°F Heating Public Area: 75°F cooling /70°F heating
| Thermostat Setback | Setback is based on codes and standards |  |  | Applicable codes or standards
| Supply air temperature | For the VAV system, the supply air temperature is set at 55 F. Temperature reset may be required by codes and standards. For the DOAS, the supply air temperature is reset according to the outdoor air temperature: Tsupply = 60 F when Toa < 60 F; Tsupply = 55 F when Toa > 70 F; Interpolation when Toa is between 60 and 70 F. |  |  | Applicable codes or standards
| Chilled water supply temperatures | 44 F. Temperature reset may be required by codes and standards. |  |  | Applicable codes or standards
| Hot water supply temperatures | 140 F. Temperature reset may be required by codes and standards. |  |  | Applicable codes or standards
| Economizers | Requirements in codes or standards |  |  | Applicable codes or standards
| Ventilation | ASHRAE Standard 62.1 or International Mechanical Code See under Outdoor Air |  |  | Applicable codes or standards
| Demand Control Ventilation | Requirements in codes or standards |  |  | Applicable codes or standards
| Energy Recovery | Requirements in codes or standards |  |  | Applicable codes or standards
Supply Fan
| Fan schedules | See under Schedules
| Fan Mechanical Efficiency (%) | Fan coil unit: 65% VAV and DOAS System fans: depending on the fan motor size and requirements in codes or standards |  |  | Requirements in applicable codes or standards for motor efficiency and fan power limitation
| Fan Pressure Drop | Fan coil unit: 1.33 in. w.c. VAV and DOAS system: depending on the fan supply air cfm
Exhaust Fan
| Fan schedules | See under Schedules
| Fan Total Efficiency (%) | 55%
| Fan Pressure Drop | 0.5 in. w.c.
Pump
| Pump Type | Primary chilled water (CHW) pumps constant speed; secondary CHW pump: variable speed; service hot water (SWH): constant speed; hot water (HW) pump: variable speed
| Rated Pump Head | Use the pump power assumptions as specified in 90.1 Appendix G, i.e., 22 W/gpm for chilled water pump, 19 W/gpm for hot water and condensing water pumps.
| Pump Power | Autosized
Cooling Tower
| Cooling Tower Type | NA
| Cooling Tower Power | NA
Service Water Heating
| SWH type | Main and central gas water heater with storage tank Electric dishwasher booster water heater Gas water heater for laundry with storage |  |  | Reference: PNNL-23269 Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Fuel type | Natural Gas (main and laundry); Electric (dishwasher booster) |  |  | Reference: PNNL-23269 Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Thermal efficiency (%) | Requirements in codes or standards |  |  | Applicable codes or standards
| Tank Volume (gal) | 600 (main); 300 (laundry); 6 (dishwasher booster) |  |  | Reference: PNNL-23269 Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Water temperature setpoint | 140 F (main); 180 F (laundry and dishwasher booster)
| Water consumption | See under Schedules
Internal Loads & Schedules
Lighting
| Average power density (W/ft2) | Requirements in codes or standards See Zone Summary |  |  | Applicable codes or standards
| Schedule | See under Schedules
| Daylighting Controls | Requirements in codes or standards |  |  | Applicable codes or standards
| Occupancy Sensors | Requirements in codes or standards |  |  | Applicable codes or standards
Plug load
| Average power density (W/ft2) | See under Zone Summary
| Schedule | See under Schedules
Occupancy
| Average people | See under Zone Summary
| Schedule | See under Schedules
Misc.
Elevator
| Quantity |  | 6 |  | DOE Commercial Reference Building TSD (unpublished) and models (V1.3_5.0).
| Motor type |  | Traction
| Peak Motor Power Watts per elevator |  | 20370
| Heat Gain to Building |  | Exterior
| Peak Fan/lights Power Watts per elevator |  | 161.9 |  | 90.1 Mechanical Subcommittee, Elevator Working Group
| Motor and fan/lights Schedules |  | See under Schedules |  | DOE Commercial Reference Building TSD (unpublished) and models (V1.3_5.0) and Appendix DF 2007
Exterior Lighting
| Peak Power | Based on design assumptions for façade, parking lot, entrance, etc. and requirements in codes or standards |  |  | Applicable codes or standards
| Schedule | See under Schedules and control requirements in codes or standards |  |  | Applicable codes or standards
References
ASHRAE 2013. ANSI/ASHRAE Standard 169-2013. Climatic Data for Building Design Standards. American Society of Heating, Refrigerating, and Air-Conditioning Engineers, Atlanta, Georgia. Relevant information available as Annex 1 in ASHRAE 2016
McGraw-Hill Companies, Inc. (2001). Time-Saver Standards for Building Types. New York, NY.
LBNL (1991). Huang, Joe, Akbari, H., Rainer, L. and Ritschard, R. 481 Prototypical Commercial Buildings for 20 Urban Market Areas, prepared for the Gas Research Institute, Chicago IL, also LBL-29798, Berkeley CA.
PNNL's CBECS Study. 2007. Analysis of Building Envelope Construction in 2003 CBECS Buildings. Dave Winiarski, Mark Halverson, and Wei Jiang. Pacific Northwest National Laboratory. March 2007.
PNNL's CBECS Study. 2006. Review of Pre- and Post-1980 Buildings in CBECS – HVAC Equipment. Dave Winiarski, Wei Jiang and Mark Halverson. Pacific Northwest National Laboratory. December 2006.
Ducker International Standard. 2001. 2000 U.S. Market For Residential and Specialty Air Conditioning: PTAC.
Sachs, H., 2005. Opportunities for Elevator Energy Efficiency Improvements, ACEEE.
Wassmer and Brandemuehl, 2006, Effect of Data Availability on Modeling of Residential Air Conditioners and Heat Pumps for Energy Calculations
Goel S, M Rosenberg, R Athalye, Y Xie, W Wang, R Hart, J Zhang, V Mendon. 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models. PNNL-23269, Pacific Northwest National Laboratory, Richland, Washington. http://www.pnnl.gov/main/publications/external/technical_reports/PNNL-23269.pdf

## Zone Summary
Zone Summary
Zone | Area [ft²] | Conditioned [Y/N] | Volume [ft³] | Multipliers | Gross Wall Area [ft²] | Window Glass Area [ft²] | Lighting1 [W/ft²] | People [ft²/person] | Number of People | Plug and Process [W/ft²]
BASEMENT | 21299.8204 | Y | 170441.5184 | 1 | 0 | 0 | 0.99964 | 400.0921 | 106.4991 | 0.49982
RETAIL_1_FLR_1 | 721.9311 | Y | 9385.1409 | 1 | 740.9831 | 250.7976 | 1.4995 | 124.9682 | 10.829 | 0.99964
RETAIL_2_FLR_1 | 836.0279 | Y | 10868.3435 | 1 | 285.9954 | 0 | 1.4995 | 124.9682 | 12.5404 | 0.99964
MECH_FLR_1 | 1767.854 | Y | 22982.5772 | 1 | 675.9695 | 0 | 1.4995 | 0 | 0 | 0.49982
STORAGE_FLR_1 | 1019.982 | Y | 13259.4779 | 1 | 389.9741 | 0 | 0.89931 | 500.6265 | 0 | 0.24991
LAUNDRY_FLR_1 | 840.0105 | Y | 10919.9024 | 1 | 922.9998 | 0 | 0.60016 | 249.7212 | 8.4001 | 55.53
CAFE_FLR_1 | 2032.8599 | Y | 26427.4917 | 1 | 1637.9344 | 706.3235 | 1.2997 | 14.9617 | 142.3002 | 0.49982
LOBBY_FLR_1 | 14081.155 | Y | 183054.0375 | 1 | 4680.0124 | 917.5102 | 1.1 | 33.3679 | 422.4347 | 0.74973
ROOM_1_FLR_3 | 420.0053 | Y | 4200.2885 | 4 | 430.0156 | 141.8675 | 1.1 | 279.9676 | 1.5 | 0.6271
ROOM_2_FLR_3 | 420.0053 | Y | 4199.9353 | 4 | 430.0156 | 141.8675 | 1.1 | 279.9676 | 1.5 | 0.6271
ROOM_3_MULT19_FLR_3 | 263.9295 | Y | 2639.7475 | 76 | 120.0169 | 39.611 | 1.1 | 175.9889 | 1.5 | 0.97735
ROOM_4_MULT19_FLR_3 | 264.0371 | Y | 2640.4537 | 76 | 120.0169 | 39.611 | 1.1 | 175.9889 | 1.5 | 0.97735
ROOM_5_FLR_3 | 420.0053 | Y | 4200.2885 | 4 | 430.0156 | 141.8675 | 1.1 | 279.9676 | 1.5 | 0.6271
ROOM_6_FLR_3 | 420.0053 | Y | 4199.9353 | 4 | 430.0156 | 141.8675 | 1.1 | 279.9676 | 1.5 | 0.6271
CORRIDOR_FLR_3 | 4191.4414 | Y | 41914.9518 | 4 | 520.0014 | 171.5757 | 0.49982 | 996.6245 | 0 | 0
ROOM_1_FLR_6 | 420.0053 | Y | 4200.2885 | 1 | 430.0156 | 141.9751 | 1.1 | 279.9676 | 1.5 | 0.6271
ROOM_2_FLR_6 | 420.0053 | Y | 4199.9353 | 1 | 430.0156 | 141.9751 | 1.1 | 279.9676 | 1.5 | 0.6271
ROOM_3_MULT9_FLR_6 | 264.0371 | Y | 2640.4537 | 9 | 220.013 | 72.656 | 1.1 | 175.9889 | 1.5 | 0.97735
BANQUET_FLR_6 | 3569.937 | Y | 35698.9204 | 1 | 1050.0131 | 346.7035 | 1.2997 | 14.9617 | 249.8956 | 6.303
DINING_FLR_6 | 3569.937 | Y | 35698.9204 | 1 | 1050.0131 | 346.7035 | 1.2997 | 14.9617 | 249.8956 | 6.303
KITCHEN_FLR_6 | 1111.9052 | Y | 11119.4285 | 1 | 940.0066 | 283.9502 | 1.1994 | 200.0999 | 22.2381 | 272.68
CORRIDOR_FLR_6 | 4435.996 | Y | 44360.4704 | 1 | 919.9859 | 303.7557 | 0.49982 | 996.6245 | 0 | 0
TOTAL | 122115.0736 |  | 1242537.4249 |  | 43336.8565 | 13070.6452 |  |  | 1493.5327
AREA WEIGHTED AVERAGE | [6 empty] | 0.99995 | 335.6932 |  | 3.8164
1. Listed lighting power density is based on applicable requirements in ASHRAE Standard 90.1-2004. The actual inputs for the models are based on appliable codes and standards

## Outdoor Air
Minimum Outdoor Ventilation Air Requirements
|  |  |  | Total Occupants | Total OSA Ventilation (cfm/zone) |  |  | Total OSA Ventilation (cfm/ft2)
Zone | Area (ft2) | Multiplier | Assumed Space Type | 62.1-2004 1,2,3 | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007) | 90.1-2004 (62-1999) | 90.1-2007 (62.1-2004) | 90.1-2010 (62.1-2007)
BASEMENT | 21299.8204 | 1 | Office space | 106.4991 | 2129.982 | 1810.4847 | 1810.4847 | 0.1 | 0.085 | 0.085
RETAIL_1_FLR_1 | 721.9311 | 1 | Sales (except as below) | 10.829 | 216.5793 | 167.849 | 167.849 | 0.3 | 0.2325 | 0.2325
RETAIL_2_FLR_1 | 836.0279 | 1 | Sales (except as below) | 12.5404 | 250.8084 | 194.3765 | 194.3765 | 0.3 | 0.2325 | 0.2325
MECH_FLR_1 | 1767.854 | 1 |  | 0 | NA | NA | NA | NA | NA | NA
STORAGE_FLR_1 | 1019.982 | 1 | Storage rooms | 0 | 152.9973 | 122.3978 | 122.3978 | 0.15 | 0.12 | 0.12
LAUNDRY_FLR_1 | 840.0105 | 1 | Commercial laundry | 8.4001 | 210.0026 | 0 | 0 | 0.25 | 0 | 0
CAFE_FLR_1 | 2032.8599 | 1 | Restaurant dining rooms | 142.3002 | 2846.0038 | 1433.1662 | 1433.1662 | 1.4 | 0.705 | 0.705
LOBBY_FLR_1 | 14081.155 | 1 | Lobbies/prefunction (hotel, motel, resort, dorm) | 422.4347 | 6336.5198 | 4013.1292 | 4013.1292 | 0.45 | 0.285 | 0.285
ROOM_1_FLR_3 | 420.0053 | 4 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 60 | 32.7013 | 32.7013 | 0.14286 | 0.077859 | 0.077859
ROOM_2_FLR_3 | 420.0053 | 4 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 60 | 32.7013 | 32.7013 | 0.14286 | 0.077859 | 0.077859
ROOM_3_MULT19_FLR_3 | 263.9295 | 76 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 35 | 23.3342 | 23.3342 | 0.13261 | 0.088411 | 0.088411
ROOM_4_MULT19_FLR_3 | 264.0371 | 76 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 35 | 23.3438 | 23.3438 | 0.13256 | 0.088411 | 0.088411
ROOM_5_FLR_3 | 420.0053 | 4 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 60 | 32.7013 | 32.7013 | 0.14286 | 0.077859 | 0.077859
ROOM_6_FLR_3 | 420.0053 | 4 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 60 | 32.7013 | 32.7013 | 0.14286 | 0.077859 | 0.077859
CORRIDOR_FLR_3 | 4191.4414 | 4 | Corridors (public spaces) | 0 | 209.5721 | 251.4865 | 251.4865 | 0.05 | 0.06 | 0.06
ROOM_1_FLR_6 | 420.0053 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 60 | 32.7013 | 32.7013 | 0.14286 | 0.077859 | 0.077859
ROOM_2_FLR_6 | 420.0053 | 1 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 60 | 32.7013 | 32.7013 | 0.14286 | 0.077859 | 0.077859
ROOM_3_MULT9_FLR_6 | 264.0371 | 9 | Bedroom/Living Room (hotel/motel/dorm) | 1.5 | 35 | 23.3438 | 23.3438 | 0.13256 | 0.088411 | 0.088411
BANQUET_FLR_6 | 3569.937 | 1 | Restaurant dining rooms | 249.8956 | 4997.9118 | 2516.8056 | 2516.8056 | 1.4 | 0.705 | 0.705
DINING_FLR_6 | 3569.937 | 1 | Restaurant dining rooms | 249.8956 | 4997.9118 | 2516.8056 | 2516.8056 | 1.4 | 0.705 | 0.705
KITCHEN_FLR_6 | 1111.9052 | 1 | Kitchen | 22.2381 | 333.5716 | 778.3337 | 778.3337 | 0.3 | 0.7 | 0.7
CORRIDOR_FLR_6 | 4435.996 | 1 | Corridors (public spaces) | 0 | 221.7998 | 266.1598 | 266.1598 | 0.05 | 0.06 | 0.06
TOTAL | 122115.0736 |  |  | 1493.5327 | 30247.3765 | 19171.6985 | 19171.6985 | 0.2477 | 0.157 | 0.157
1. Assume each guestroom and suite contains 1.5 persons averagely based on inputs from AEDG-Highway Lodging project committee.
2. Laundry occupancy not included in ASHRAE 62.1-2004, therefore occupancy based on ASHRAE 66-1999.
3. Kitchen occupancy not included in ASHRAE 62.1, 2004, therefore occupancy based on ASHRAE 62-1999.
4. Each "Room" zone of 264 sft contains one guestroom with one bedroom and one bath. Each "Room" zone of 420 sft contains one guest suite with one bedroom, one living room, and one bath. ASHRAE 62-1999 requires 30 cfm per each living room and each bedroom and 35 cfm per bath, regardless of area. For bathroom, the 35 cfm OA requirement is the installed capacity for intermittent use. Based on the interpretation from ASHRAE (http://www.ashrae.org/technology/page/913), the 35 cfm of outdoor air can be supplied to the hotel/motel bedroom then exhausted through the bathroom at the same rate, this would meet the standard for both the bedroom and the bathroom. So, we should use a ventilation rate of 35 cfm for guestroom, not 65 cfm. This is consistent with inputs from AEDG Highway Lodging project committee. Thus, the OA rate equals to 35 cfm for standard guest room and 60 cfm for suite.
5. The ventilation requirements for other codes or standards are based on their reference ASHRAE Standard 62.1 or International Mechanical Code

## Schedules
Schedule | Type | Through | Day of Week | 1 am | 2 am | 3 am | 4 am | 5 am | 6 am | 7 am | 8 am | 9 am | 10 am | 11 am | Noon | 1 pm | 2 pm | 3 pm | 4 pm | 5 pm | 6 pm | 7 pm | 8 pm | 9 pm | 10 pm | 11 pm | 12 pm
Internal Loads Schedules
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
(for public spaces) |  |  | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3
|  |  | SummerDesignDay | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesignDay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, and Other | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3
GuestRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33
(for guest rooms) |  |  | Sat, Sun, Hol | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
|  |  | SummerDesignDay CustomDay1 CustomDay2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesignDay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4
(for public spaces on the ground floor) |  |  | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4
|  |  | SummerDesignDay | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesignDay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, and Other | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4
GuestRoom_Eqp_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
(for guest rooms) |  |  | Sat, Sun, Hol | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
|  |  | SummerDesignDay CustomDay1 CustomDay2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesignDay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen_Elec_Equip_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
(for kitchen, dining and banquet) |  |  | Sat, Sun, Hol, Others | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  |  | SummerDesignDay | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  |  | WinterDesignDay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
(for kitchen) |  |  | Sun, Hol, Others | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
|  |  | SummerDesignDay | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  | WinterDesignDay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9
(for public spaces) |  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7
|  |  | SummerDesignDay | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesignDay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, and Other | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8
GUESTROOM_ OCC_SCH | Fraction | Through 12/31 | WD | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65
(for guest rooms) |  |  | Sat, Sun, Hol, others | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5
|  |  | SummerDesignDay CustomDay1 CustomDay2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesignDay | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_ELEVATORS | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
|  |  | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
|  |  | SummerDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
ELEV_LIGHT_FAN_SCH_24_7 | Fraction | Through 12/31 | WD | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen_Exhaust_SCH | fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Service Water Heater Load Schedule
BLDG_SWH_SCH | Fraction | Through 12/31 | WD,SummerDesignDay | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
|  |  | Sat, WinterDesignDay | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
|  |  | Sun, Hol, Others | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
GuestRoom_SWH_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25
|  |  | Others | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35
LaundryRoom_SWH_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Infiltration Schedule
INFIL_QUARTER_ON_SCH | fraction | Through 12/31 | WD | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
(for all zones) |  |  | Sat, Sun, Hol | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HVAC Schedules
GUESTROOM_FAN_SCH | on/off | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
(HVAC Operation)
COMMONAREA_FAN_SCH | on/off | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
(HVAC Operation)
HtgSetP_Sch | Temperature | Through 12/31 | All | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
(°F)
ClgSetP_Sch | Temperature | Through 12/31 | All | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
(°F)
MinOA_MotorizedDamper_Sched | on/off | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Laundry Exhaust Fan | on/off | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Notes: | The schedules are also subject to changes in different models based on applicable code requrirements triggered by cllimate zone, system capacity, control type, or other criteria.