## Building Description
Prototype Building Modeling Specifications
Pacific Northwest National Laboratory, updated on October 18, 2018
| Item | Descriptions |  |  | Data Source
Program
| Vintage | NEW CONSTRUCTION
| Location (Representing 8 Climate Zones) | Zone 1A: Honolulu, Hawaii (very hot, humid) Zone 1B: New Delhi, India (very hot, dry) Zone 2A: Tampa, Florida (hot, humid) Zone 2B: Tucson, Arizona (hot, dry) Zone 3A: Atlanta, Georgia (warm, humid) Zone 3B: El Paso, Texas (warm, dry) Zone 3C: San Diego, California (warm, marine) | Zone 4A: New York, New York (mixed, humid) Zone 4B: Albuquerque, New Mexico (mixed, dry) Zone 4C: Seattle, Washington (mixed, marine) Zone 5A: Buffalo, NY (cool, humid) Zone 5B: Denver, Colorado (cool, dry) Zone 5C: Port Angeles, Washington (cool, marine) | Zone 6A: Rochester, Minnesota (cold, humid) Zone 6B: Great Falls, Montana (cold, dry) Zone 7: International Falls, Minnesota (very cold) Zone 8: Fairbanks, Alaska (subarctic | Selection of representative climates based on ASHRAE Standard 169-2013
| Available fuel types | Gas, electricity
| Building Type (Principal Building Function) | Education
| Building Prototype | Secondary School
Form
| Total Floor Area (sq feet) | 210,900 (340 ft x 460 ft)
Building shape
| Aspect Ratio | 1.4
| Number of Floors | 2
| Window Fraction (Window-to-Wall Ratio) | 33% Ribbon window across all facades on both floors
| Window Locations | Continuous Band
| Shading Geometry | None
| Azimuth | Non-directional
| Thermal Zoning | Classrooms zoned by exposure. Corner classrooms separated out from single exposure classrooms. Double loaded corridors zoned separately. Administrative areas zoned by exposure. Gymnasium , auxiliary gym, auditorium, kitchen, and cafeteria are single zones. See Zone Summary.
| Floor to floor height (feet) | 13
| Floor to ceiling height (feet) | 13
| Glazing sill height (feet) | 3.6 (top of the window is 8.1 ft high with 4.5 ft high glass)
Architecture
Exterior walls
| Construction | Steel-Framed Walls (2X4 16IN OC) 0.4 in. Stucco+5/8 in. gypsum board + wall Insulation+5/8 in |  |  | Construction type: 2003 CBECS Data and PNNL's CBECS Study 2007. Exterior wall layers: default 90.1 layering
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; Walls, Above-Grade, Steel-Framed |  |  | Applicable codes or standards
| Dimensions | Based on floor area and aspect ratio
| Tilts and orientations | Vertical
Roof
| Construction | Built-up Roof: Roof membrane+Roof insulation+metal decking |  |  | Construction type: 2003 CBECS Data and PNNL's CBECS Study 2007. Roof layers: default 90.1 layering
| U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; Roofs, Insulation entirely above deck |  |  | Applicable codes or standards
| Dimensions | Based on floor area and aspect ratio
| Tilts and orientations | Horizontal
Window
| Dimensions | Based on window fraction, location, glazing sill height, floor area and aspect ratio
| Glass-Type and frame | Hypothetical window with weighted U-factor and SHGC
| U-factor (Btu / h * ft2 * °F) | Requirements in codes or standards Nonresidential; Vertical Glazing |  |  | Applicable codes or standards
SHGC (all)
Visible transmittance
| Operable area | 35% |  |  | PNNL 's Glazing Market Data for ASHRAE spreadsheet
Skylight
| Dimensions | Gymnasium Auxiliary Gymnasium | (4 ft x 4 ft) x 54 skylights = 864 ft2 of total skylight area (4 ft x 4 ft) x 36 skylights = 576 ft2 of total skylight area | 4% of Gym roof area 4.3% of Aux. Gym roof area | AEDG K-12 Guide
| Glass-Type and frame | Hypothetical glass and frame meeting requirements in codes or standards below
| U-factor (Btu / h * ft2 * °F) | Requirements in codes or standards Nonresidential; Skylight with curb, Glass, 2.1-5% |  |  | Applicable codes or standards
SHGC
Visible transmittance
Foundation
| Foundation Type | Slab-on-grade floors (unheated)
| Construction | 6" concrete slab poured directly on to the earth + carpet
| Thermal properties for ground level floor U-factor (Btu / h * ft2 * °F) and/or R-value (h * ft2 * °F / Btu) | Requirements in codes or standards Nonresidential; Slab-on-Grade Floors, unheated |  |  | Applicable codes or standards
| Thermal properties for basement walls | NA
| Dimensions | Based on floor area and aspect ratio
Interior Partitions
| Construction | 2 x 4 uninsulated steel stud wall
| Dimensions | based on floor plan and floor-to-floor height
| Internal Mass | 6 inches standard wood (16.6 lb/ft²)
Air Barrier System
| Infiltration | Peak: 0.2016 cfm/sf of above grade exterior wall surface area, adjusted by wind (when fans turn off) Off Peak: 25% of peak infiltration rate (when fans turn on) Additional infiltration through building entrance |  |  | Reference: PNNL-18898. Infiltration Modeling Guidelines for Commercial Building Energy Analysis. PNNL-20026. Energy Saving Impact of ASHRAE 90.1 Vestibule Requirements: Modeling of Air Infiltration through Door Openings. Modeled peak infiltration rate may be different for different codes or standards because of their continuous air barrier requirements.
HVAC
System Type
| Heating type | 1. Gas furnaces inside packaged air conditioning units 2. Gas-fired boiler provide heating hot water and chilled water to these AHUs. |  |  | 2003 CBECS Data, PNNL's CBECS Study 2006, and 90.1 Mechanical Subcommittee input.
| Cooling type | 1. Packaged air conditioner 2. Air-cooled Chiller
| Distribution and terminal units | 1. CAV system: direct air from the packaged unit 2. VAV System: VAV terminal box with damper and hot water reheating coil Zone Control Type: minimum supply air at 30% of the zone design peak supply air
HVAC Sizing
| Air Conditioning | Autosized to design day
| Heating | Autosized to design day
HVAC Efficiency
| Air Conditioning | Various by climate location and design cooling capacity Requirements in codes or standards Minimum equipment efficiency for Air Conditioners and Condensing Units Minimum equipment efficiency for Air-cooled Chillers |  |  | Applicable codes or standards
| Heating | Various by climate location and design heating capacity Requirements in codes or standards Minimum equipment efficiency for Warm Air Furnaces Minimum equipment efficiency for Gas and Oil-fired Boilers |  |  | Applicable codes or standards
HVAC Control
| Thermostat Setpoint | 75°F Cooling/70°F Heating
| Thermostat Setback | 85°F Cooling/60°F Heating
| Supply air temperature | Minimum 50 °F, maximum 122 °F
| Chilled water supply temperatures | 44 °F
| Hot water supply temperatures | 180 °F
| Economizers | Requirements in codes or standards |  |  | Applicable codes or standards
| Ventilation | ASHRAE Standard 62.1 or International Mechanical Code See under Outdoor Air. |  |  | Applicable codes or standards
| Demand Control Ventilation | Requirements in codes or standards |  |  | Applicable codes or standards
| Energy Recovery | Requirements in codes or standards |  |  | Applicable codes or standards
Supply Fan
| Fan schedules | See under Schedules
| Supply Fan Mechanical Efficiency (%) | Depending on the fan motor size and requirements in codes or standards |  |  | Requirements in applicable codes or standards for motor efficiency and fan power limitation
| Supply Fan Pressure Drop | Depending on the fan supply air cfm
Pump
| Pump Type | Variable speed
| Rated Pump Head | CW: 75 ft HW: 60 ft
| Pump Power | Autosized
Cooling Tower
| Cooling Tower Type | NA
| Cooling Tower Power | NA
Service Water Heating
| SWH type | Storage tank
| Fuel type | Natural gas (main); electric (dishwasher booster) |  |  | Reference: PNNL 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Thermal efficiency (%) | Requirements in codes or standards |  |  | Applicable codes or standards
| Tank Volume (gal) | 600 (main); 6 (dishwasher booster) |  |  | Reference: PNNL 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models
| Water temperature setpoint | 140 F (main); 180 F (dishwasher booster)
| Water consumption | See under Schedules
Internal Loads & Schedules
Lighting
| Average power density (W/ft2) | Requirements in codes or standards See Zone Summary |  |  | Applicable codes or standards
| Schedule | See under Schedules
| Daylighting Controls | Requirements in codes or standards |  |  | Applicable codes or standards
| Occupancy Sensors | Requirements in codes or standards |  |  | Applicable codes or standards
Plug load
| Average power density (W/ft2) | See under Zone Summary
| Schedule | See under Schedules
Electric load (cooking)
| Average power density (W/ft2) | 20.6 W/ft2 - 30% Radiant fraction , 25% latent, 20% lost
| Schedule | See under Schedules
Gas Equip Cooking
| Average power density (W/ft2) | 156 W/ft2 - 20% Radiant fraction , 10% latent, 70% lost
| Schedule | See under Schedules
Refrigeration
| Equipment | Walk-in freezer and display case both with air-cooled local condensers
Occupancy
| Average people | See under Zone Summary |  |  | User's Manual for ASHRAE Standard 90.1-2004 (Appendix G)
| Schedule | See under Schedules
Misc.
Elevator
| Quantity |  | 2 |  | DOE Commercial Reference Building TSD (unpublished) and models (V1.3_5.0).
| Motor type |  | hydraulic
| Peak Motor Power Watts per elevator |  | 16055
| Heat Gain to Building |  | Interior
| Peak Fan/lights Power Watts per elevator |  | 161.9 |  | 90.1 Mechanical Subcommittee, Elevator Working Group
| Motor and fan/lights Schedules |  | See under Schedules |  | DOE Commercial Reference Building TSD (unpublished) and models (V1.3_5.0) and Appendix DF 2007
Exterior Lighting
| Peak Power | Based on design assumptions for façade, parking lot, entrance, etc. and requirements in codes or standards |  |  | Applicable codes or standards
| Schedule | See under Schedules and control requirements in codes or standards |  |  | Applicable codes or standards
References
ASHRAE 2013. ANSI/ASHRAE Standard 169-2013. Climatic Data for Building Design Standards. American Society of Heating, Refrigerating, and Air-Conditioning Engineers, Atlanta, Georgia. Relevant information available as Annex 1 in ASHRAE 2016
PNNL's CBECS Study. 2007. Analysis of Building Envelope Construction in 2003 CBECS Buildings. Dave Winiarski, Mark Halverson, and Wei Jiang. Pacific Northwest National Laboratory. March 2007.
PNNL's CBECS Study. 2006. Review of Pre- and Post-1980 Buildings in CBECS – HVAC Equipment. Dave Winiarski, Wei Jiang and Mark Halverson. Pacific Northwest National Laboratory. December 2006.
“Study of the U.S. Market For Windows, Doors, and Skylights”, American Architectural Manufacturers Association, Window & Door Manufacturers Association, 2006.
Goel S, M Rosenberg, R Athalye, Y Xie, W Wang, R Hart, J Zhang, V Mendon. 2014. Enhancements to ASHRAE Standard 90.1 Prototype Building Models. PNNL-23269, Pacific Northwest National Laboratory, Richland, Washington. http://www.pnnl.gov/main/publications/external/technical_reports/PNNL-23269.pdf

## Zone Summary
Zone Summary
(90.1-2004 baseline requirements for LPD)
Zone Name | Area [ft²] | Conditioned [Y/N] | Volume [ft³] | Multipliers | Gross Wall Area [ft²] | Window Glass Area [ft²] | Lighting [W/ft²] | People [ft²/person] | Number of People | Plug and Process [W/ft²]
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 1065.7308 | Yes | 13986.508 | 1 | 861.1966 | 301.4188 | 1.3999 | 28.5271 | 37.3585 | 0.92894
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 1065.7308 | Yes | 13986.508 | 1 | 861.1966 | 301.4188 | 1.3999 | 28.5271 | 37.3585 | 0.92894
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 5134.8849 | Yes | 67389.5384 | 1 | 2282.1711 | 798.7599 | 1.3999 | 28.5271 | 180 | 0.92894
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 5134.8849 | Yes | 67389.5384 | 1 | 2282.1711 | 798.7599 | 1.3999 | 28.5271 | 180 | 0.92894
CORRIDOR_POD_1_ZN_1_FLR_1 | 3444.7865 | Yes | 45208.9146 | 1 | 215.2992 | 75.3547 | 0.49996 | 0 | - | 0.37158
CORRIDOR_POD_1_ZN_1_FLR_2 | 3444.7865 | Yes | 45208.9146 | 1 | 215.2992 | 75.3547 | 0.49996 | 0 | - | 0.37158
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 1065.7308 | Yes | 13986.508 | 1 | 861.1966 | 301.4188 | 1.3999 | 28.5271 | 37.3585 | 0.92894
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 1065.7308 | Yes | 13986.508 | 1 | 861.1966 | 301.4188 | 1.3999 | 28.5271 | 37.3585 | 0.92894
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 5134.8849 | Yes | 67389.5384 | 1 | 2282.1711 | 798.7599 | 1.3999 | 28.5271 | 180 | 0.92894
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 5134.8849 | Yes | 67389.5384 | 1 | 2282.1711 | 798.7599 | 1.3999 | 28.5271 | 180 | 0.92894
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 1065.7308 | Yes | 13986.508 | 1 | 861.1966 | 301.4188 | 1.3999 | 28.5271 | 37.3585 | 0.92894
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 1065.7308 | Yes | 13986.508 | 1 | 861.1966 | 301.4188 | 1.3999 | 28.5271 | 37.3585 | 0.92894
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 5134.8849 | Yes | 67389.5384 | 1 | 2282.1711 | 798.7599 | 1.3999 | 28.5271 | 180 | 0.92894
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 5134.8849 | Yes | 67389.5384 | 1 | 2282.1711 | 798.7599 | 1.3999 | 28.5271 | 180 | 0.92894
CORRIDOR_POD_2_ZN_1_FLR_1 | 3444.7865 | Yes | 45208.9146 | 1 | 215.2992 | 75.3547 | 0.49996 | 0 | - | 0.37158
CORRIDOR_POD_2_ZN_1_FLR_2 | 3444.7865 | Yes | 45208.9146 | 1 | 215.2992 | 75.3547 | 0.49996 | 0 | - | 0.37158
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 1065.7308 | Yes | 13986.508 | 1 | 861.1966 | 301.4188 | 1.3999 | 28.5271 | 37.3585 | 0.92894
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 1065.7308 | Yes | 13986.508 | 1 | 861.1966 | 301.4188 | 1.3999 | 28.5271 | 37.3585 | 0.92894
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 5134.8849 | Yes | 67389.5384 | 1 | 2282.1711 | 798.7599 | 1.3999 | 28.5271 | 180 | 0.92894
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 5134.8849 | Yes | 67389.5384 | 1 | 2282.1711 | 798.7599 | 1.3999 | 28.5271 | 180 | 0.92894
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 1065.7308 | Yes | 13986.508 | 1 | 861.1966 | 301.4188 | 1.3999 | 28.5271 | 37.3585 | 0.92894
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 1065.7308 | Yes | 13986.508 | 1 | 861.1966 | 301.4188 | 1.3999 | 28.5271 | 37.3585 | 0.92894
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 5134.8849 | Yes | 67389.5384 | 1 | 2282.1711 | 798.7599 | 1.3999 | 28.5271 | 180 | 0.92894
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 5134.8849 | Yes | 67389.5384 | 1 | 2282.1711 | 798.7599 | 1.3999 | 28.5271 | 180 | 1.8579
CORRIDOR_POD_3_ZN_1_FLR_1 | 3444.7865 | Yes | 45208.9146 | 1 | 215.2992 | 75.3547 | 0.49996 | 0 | - | 0.37158
CORRIDOR_POD_3_ZN_1_FLR_2 | 3444.7865 | Yes | 45208.9146 | 1 | 215.2992 | 75.3547 | 0.49996 | 0 | - | 0.37158
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 1065.7308 | Yes | 13986.508 | 1 | 861.1966 | 301.4188 | 1.3999 | 28.5271 | 37.3585 | 0.92894
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 1065.7308 | Yes | 13986.508 | 1 | 861.1966 | 301.4188 | 1.3999 | 28.5271 | 37.3585 | 0.92894
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 5134.8849 | Yes | 67389.5384 | 1 | 2282.1711 | 798.7599 | 1.3999 | 28.5271 | 180 | 0.92894
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 5134.8849 | Yes | 67389.5384 | 1 | 2282.1711 | 798.7599 | 1.3999 | 28.5271 | 180 | 1.8579
MAIN_CORRIDOR_ZN_1_FLR_1 | 12272.052 | Yes | 161056.7584 | 1 | 2152.9916 | 527.4829 | 0.49996 | 0 | - | 0.37158
MAIN_CORRIDOR_ZN_1_FLR_2 | 12272.052 | Yes | 161056.7584 | 1 | 2152.9916 | 527.4829 | 0.49996 | 0 | - | 0.37158
LOBBY_ZN_1_FLR_1 | 2260.6412 | Yes | 29668.3502 | 1 | 645.8975 | 226.0641 | 1.2999 | 0 | - | 0.37158
LOBBY_ZN_1_FLR_2 | 2260.6412 | Yes | 29668.3502 | 1 | 645.8975 | 226.0641 | 1.2999 | 0 | - | 0.37158
BATHROOMS_ZN_1_FLR_1 | 2260.6412 | Yes | 29668.3502 | 1 | 1248.7351 | 271.2769 | 0.89991 | 0 | - | 0.37158
BATHROOMS_ZN_1_FLR_2 | 2260.6412 | Yes | 29668.3502 | 1 | 1248.7351 | 271.2769 | 0.89991 | 0 | - | 0.37158
OFFICES_ZN_1_FLR_1 | 5726.9576 | Yes | 75159.8206 | 1 | 2239.1112 | 783.6889 | 1.0999 | 200.0129 | 28.6329 | 1.0033
OFFICES_ZN_1_FLR_2 | 5726.9576 | Yes | 75159.8206 | 1 | 2239.1112 | 783.6889 | 1.0999 | 200.0129 | 28.6329 | 1.0033
GYM_ZN_1_FLR_1 | 21271.5568 | Yes | 558330.0957 | 1 | 0 | 864.2108 | 1.3999 | 33.3714 | 637.4194 | 0.46447
AUX_GYM_ZN_1_FLR_1 | 13434.6675 | Yes | 352629.5341 | 1 | 6545.0944 | 2867.2465 | 1.3999 | 33.3714 | 402.5806 | 0.46447
AUDITORIUM_ZN_1_FLR_1 | 10635.7784 | Yes | 279165.0479 | 1 | 5511.6584 | 1145.3915 | 0.89991 | 6.6743 | 1593.5484 | 0.46447
KITCHEN_ZN_1_FLR_1 | 2325.2309 | Yes | 30516.0174 | 1 | 387.5385 | 135.6385 | 1.1999 | 66.4198 | 35.0081 | 177.0238
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 9042.5646 | Yes | 118673.4009 | 1 | 2540.5301 | 893.5992 | 1.2999 | 100.0065 | 90.4198 | 0.92894
CAFETERIA_ZN_1_FLR_1 | 6717.3337 | Yes | 88157.3835 | 1 | 2152.9916 | 753.5471 | 0.89991 | 10.0114 | 670.9677 | 7.1463
MECH_ZN_1_FLR_1 | 3681.6156 | Yes | 48317.0275 | 1 | 0 | 0 | 1.4999 | 0 | - | 9.1812
MECH_ZN_1_FLR_2 | 3681.6156 | Yes | 48317.0275 | 1 | 0 | 0 | 1.4999 | 0 | - | 0.37158
TOTAL | 210907.0554 |  | 3362978.1373 |  | 68723.4913 | 23930.932 |  |  | 6095.5118
AREA WEIGHTED AVERAGE | [6 empty] | 1.1337 | 32.0935 |  | 3.0087
1. Listed lighting power density is based on applicable requirements in ASHRAE Standard 90.1-2004. The actual inputs for the models are based on appliable codes and standards

## Outdoor Air
Minimum Outdoor Ventilation Air Requirements
|  |  |  | Total Occupants | Total OSA Ventilation (cfm/zone) |  |  | Total OSA Ventilation (cfm/sqft)
Zone | Area (ft2) | Multipliers | Assumed Space Type | 62.1-2004 | 62-1999 | 62.1-2004 | 90.1-2010 (62.1-2007) | 62-1999 | 62.1-2004 | 90.1-2010 (62.1-2007)
CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 1065.7 | 1 | Classrooms (age 9 plus) | 37.2995 | 559.4925 | 500.879 | 500.879 | 0.525 | 0.47 | 0.47
CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 1065.7 | 1 | Classrooms (age 9 plus) | 37.2995 | 559.4925 | 500.879 | 500.879 | 0.525 | 0.47 | 0.47
MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 5134.9 | 1 | Classrooms (age 9 plus) | 179.7215 | 2695.8225 | 2413.403 | 2413.403 | 0.525 | 0.47 | 0.47
MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 5134.9 | 1 | Classrooms (age 9 plus) | 179.7215 | 2695.8225 | 2413.403 | 2413.403 | 0.525 | 0.47 | 0.47
CORRIDOR_POD_1_ZN_1_FLR_1 | 3444.8 | 1 | Corridors (school) | 0 | 344.48 | 206.688 | 206.688 | 0.1 | 0.06 | 0.06
CORRIDOR_POD_1_ZN_1_FLR_2 | 3444.8 | 1 | Corridors (school) | 0 | 344.48 | 206.688 | 206.688 | 0.1 | 0.06 | 0.06
CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 1065.7 | 1 | Classrooms (age 9 plus) | 37.2995 | 559.4925 | 500.879 | 500.879 | 0.525 | 0.47 | 0.47
CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 1065.7 | 1 | Classrooms (age 9 plus) | 37.2995 | 559.4925 | 500.879 | 500.879 | 0.525 | 0.47 | 0.47
MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 5134.9 | 1 | Classrooms (age 9 plus) | 179.7215 | 2695.8225 | 2413.403 | 2413.403 | 0.525 | 0.47 | 0.47
MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 5134.9 | 1 | Classrooms (age 9 plus) | 179.7215 | 2695.8225 | 2413.403 | 2413.403 | 0.525 | 0.47 | 0.47
CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 1065.7 | 1 | Classrooms (age 9 plus) | 37.2995 | 559.4925 | 500.879 | 500.879 | 0.525 | 0.47 | 0.47
CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 1065.7 | 1 | Classrooms (age 9 plus) | 37.2995 | 559.4925 | 500.879 | 500.879 | 0.525 | 0.47 | 0.47
MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 5134.9 | 1 | Classrooms (age 9 plus) | 179.7215 | 2695.8225 | 2413.403 | 2413.403 | 0.525 | 0.47 | 0.47
MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 5134.9 | 1 | Classrooms (age 9 plus) | 179.7215 | 2695.8225 | 2413.403 | 2413.403 | 0.525 | 0.47 | 0.47
CORRIDOR_POD_2_ZN_1_FLR_1 | 3444.8 | 1 | Corridors (school) | 0 | 344.48 | 206.688 | 206.688 | 0.1 | 0.06 | 0.06
CORRIDOR_POD_2_ZN_1_FLR_2 | 3444.8 | 1 | Corridors (school) | 0 | 344.48 | 206.688 | 206.688 | 0.1 | 0.06 | 0.06
CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 1065.7 | 1 | Classrooms (age 9 plus) | 37.2995 | 559.4925 | 500.879 | 500.879 | 0.525 | 0.47 | 0.47
CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 1065.7 | 1 | Classrooms (age 9 plus) | 37.2995 | 559.4925 | 500.879 | 500.879 | 0.525 | 0.47 | 0.47
MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 5134.9 | 1 | Classrooms (age 9 plus) | 179.7215 | 2695.8225 | 2413.403 | 2413.403 | 0.525 | 0.47 | 0.47
MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 5134.9 | 1 | Classrooms (age 9 plus) | 179.7215 | 2695.8225 | 2413.403 | 2413.403 | 0.525 | 0.47 | 0.47
CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 1065.7 | 1 | Classrooms (age 9 plus) | 37.2995 | 559.4925 | 500.879 | 500.879 | 0.525 | 0.47 | 0.47
CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 1065.7 | 1 | Classrooms (age 9 plus) | 37.2995 | 559.4925 | 500.879 | 500.879 | 0.525 | 0.47 | 0.47
MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 5134.9 | 1 | Classrooms (age 9 plus) | 179.7215 | 2695.8225 | 2413.403 | 2413.403 | 0.525 | 0.47 | 0.47
MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 5134.9 | 1 | Classrooms (age 9 plus) | 179.7215 | 2695.8225 | 2413.403 | 2413.403 | 0.525 | 0.47 | 0.47
CORRIDOR_POD_3_ZN_1_FLR_1 | 3444.8 | 1 | Corridors (school) | 0 | 344.48 | 206.688 | 206.688 | 0.1 | 0.06 | 0.06
CORRIDOR_POD_3_ZN_1_FLR_2 | 3444.8 | 1 | Corridors (school) | 0 | 344.48 | 206.688 | 206.688 | 0.1 | 0.06 | 0.06
CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 1065.7 | 1 | Classrooms (age 9 plus) | 37.2995 | 559.4925 | 500.879 | 500.879 | 0.525 | 0.47 | 0.47
CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 1065.7 | 1 | Classrooms (age 9 plus) | 37.2995 | 559.4925 | 500.879 | 500.879 | 0.525 | 0.47 | 0.47
MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 5134.9 | 1 | Classrooms (age 9 plus) | 179.7215 | 2695.8225 | 2413.403 | 2413.403 | 0.525 | 0.47 | 0.47
MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 5134.9 | 1 | Classrooms (age 9 plus) | 179.7215 | 2695.8225 | 2413.403 | 2413.403 | 0.525 | 0.47 | 0.47
MAIN_CORRIDOR_ZN_1_FLR_1 | 12272.1 | 1 | Corridors (school) | 0 | 1227.21 | 736.326 | 736.326 | 0.1 | 0.06 | 0.06
MAIN_CORRIDOR_ZN_1_FLR_2 | 12272.1 | 1 | Corridors (school) | 0 | 1227.21 | 736.326 | 736.326 | 0.1 | 0.06 | 0.06
LOBBY_ZN_1_FLR_1 | 2260.7 | 1 | Corridors (school) | 0 | 226.07 | 135.642 | 135.642 | 0.1 | 0.06 | 0.06
LOBBY_ZN_1_FLR_2 | 2260.7 | 1 | Corridors (school) | 0 | 226.07 | 135.642 | 135.642 | 0.1 | 0.06 | 0.06
BATHROOMS_ZN_1_FLR_1 | 2260.7 | 1 | Restroom | 0 | 0 | 0 | 0 | 0 | 0 | 0
BATHROOMS_ZN_1_FLR_2 | 2260.7 | 1 | Restroom | 0 | 0 | 0 | 0 | 0 | 0 | 0
OFFICES_ZN_1_FLR_1 | 5727 | 1 | Office space | 28.635 | 572.7 | 486.795 | 486.795 | 0.1 | 0.085 | 0.085
OFFICES_ZN_1_FLR_2 | 5727 | 1 | Office space | 28.635 | 572.7 | 486.795 | 486.795 | 0.1 | 0.085 | 0.085
GYM_ZN_1_FLR_1 | 21271.6 | 1 | Gym, stadium (play area) | 638.148 | 12762.96 | 6381.48 | 6381.48 | 0.6 | 0.3 | 0.3
AUX_GYM_ZN_1_FLR_1 | 13434.7 | 1 | Gym, stadium (play area) | 403.041 | 8060.82 | 4030.41 | 4030.41 | 0.6 | 0.3 | 0.3
AUDITORIUM_ZN_1_FLR_1 | 10635.8 | 1 | Auditorium seating area | 1595.37 | 23930.55 | 8614.998 | 8614.998 | 2.25 | 0.81 | 0.81
KITCHEN_ZN_1_FLR_1 | 2325.2 | 1 | Kitchen | 34.7045 | 6000 | 6000 | 6000 | 2.5804 | 2.5804 | 2.5804
LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 9042.6 | 1 | Libraries | 90.426 | 1356.39 | 1537.242 | 1537.242 | 0.15 | 0.17 | 0.17
CAFETERIA_ZN_1_FLR_1 | 6717.4 | 1 | Cafeteria / fast food dining | 671.74 | 13434.8 | 6247.182 | 6247.182 | 2 | 0.93 | 0.93
MECH_ZN_1_FLR_1 | 3681.6 | 1 |  | 0 | NA | NA | NA | NA | NA | NA
MECH_ZN_1_FLR_2 | 3681.6 | 1 |  | 0 | NA | NA | NA | NA | NA | NA
TOTAL | 210907.5 |  |  | 6094.9515 | 110728.14 | 71740.35 | 71740.35 | 0.52501 | 0.34015 | 0.34015
1. Listed lighting power density is based on applicable requirements in ASHRAE Standard 90.1-2004. The actual inputs for the models are based on appliable codes and standards
Space Type Lookup
Art classroom
Auditorium seating area
Bank vaults/safe deposit
Barber shop
Barracks sleeping areas
Bars, cocktail lounges
Beauty and nail salons
Bedroom/Living Room (hotel/motel/dorm)
Booking/waiting
Bowling alley (seating)
Cafeteria / fast food dining
Cell
Classrooms (age 9 plus)
Classrooms (ages 5-8)
Coin operated laundries
Computer (not printing)
Computer Lab.
Conference / meeting
Corridors (school)
Corridors (public spaces)
Courtrooms
Daycare (through age 4)
Dayroom
Disco/dance floors
Gambling casinos
Game arcades
Guard stations
Gym, stadium (play area)
Health club/aerobics room
Health club/weight rooms
Kitchen
Lecture Classroom
Lecture Hall (fixed seats)
Legislative chambers
Libraries
Lobbies
Lobbies/prefunction (hotel, motel, resort, dorm)
Main entry lobbies (office bldgs)3.
Mall common areas
Media Center
Multi-purpose assembly (hotel, motel, resort, dorm)
Multi-use Assembly (school)
Museums (Children’s)
Museums/Galleries
Music/theater/dance
Office space
Pet shops (animal areas)
Pharmacy (prep. area)
Photo studios
Places of religious worship
Reception areas
Restaurant dining rooms
Restroom
Sales (except as below)
Science laboratories
Shipping/Receiving
Spectator areas
Sports arena (play area)
Stages, studios
Storage rooms
Supermarket
Swimming (pool & deck)
Telephone/data entry
Transportation waiting
Warehouses
Wood/metal shop
Residiential single bedroom apartment
Commercial laundry
Patient rooms
Medical procedure
Operating rooms
Recovery and ICU
Autopsy rooms
Physical therapy

## Schedules
Schedule | Type | Through | Day of Week | 1 am | 2 am | 3 am | 4 am | 5 am | 6 am | 7 am | 8 am | 9 am | 10 am | 11 am | Noon | 1 pm | 2 pm | 3 pm | 4 pm | 5 pm | 6 pm | 7 pm | 8 pm | 9 pm | 10 pm | 11 pm | 12 pm
Internal Loads Schedules
BLDG_LIGHT_SCH | Fraction | 1/1 - 6/30 and 9/1-12/31 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
(Study Periods) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
BLDG_LIGHT_SCH | Fraction | 6/30 - 9/1 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
(Summer Holiday) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
BLDG_EQUIP_SCH_Base | Fraction | 1/1 - 6/30 and 9/1-12/31 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
(Study Periods) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
BLDG_EQUIP_SCH_BASE | Fraction | 6/30 - 9/1 | WD, SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
(Summer Holiday) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Kitchen_Elec_EQUIP_SCH | Fraction | 1/1 - 6/30 and 9/1-12/31 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
(Study Periods) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Kitchen_Elec_EQUIP_SCH | Fraction | 6/30 - 9/1 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
(Summer Holiday) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Kitchen_Gas_EQUIP_SCH | Fraction | 1/1 - 6/30 and 9/1-12/31 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
(Study Periods) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
Kitchen_Gas_EQUIP_SCH | Fraction | 6/30 - 9/1 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
(Summer Holiday) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
BLDG_ELEVATORS | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELEV_LIGHT_FAN_SCH_24_7 | Fraction | Through 12/31 | WD | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLDG_OCC_SCH | Fraction | 1/1 - 6/15 and 9/15-12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
(Study Periods) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH | Fraction | 6/15 - 9/15 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
(Summer Holiday) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_Extend | Fraction | 1/1 - 6/30 and 9/1-12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
(Study Periods) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_Extend | Fraction | 6/30 - 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0
(Summer Holiday) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Offices | Fraction | 1/1 - 6/30 and 9/1-12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
(Study Periods) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Offices | Fraction | 6/30 - 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
(Summer Holiday) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Gym | Fraction | 1/1 - 6/30 and 9/1-12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
(Study Periods) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Gym | Fraction | 6/30 - 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0
(Summer Holiday) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Auditorium | Fraction | 1/1 - 6/30 and 9/1-12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0
(Study Periods) |  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Auditorium | Fraction | 6/30 - 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0
(Summer Holiday) |  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Cafeteria | Fraction | 1/1 - 6/30 and 9/1-12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0
(Study Periods) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH_Cafeteria | Fraction | 6/30 - 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0
(Summer Holiday) |  |  | Sat, Sun, Hol, WinterDesign, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Service Water Heater Load Schedule
BLDG_SWH_SCH | Fraction | Through 6/15 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0
(Study Periods) |  |  | SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
|  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_SWH_SCH | Fraction | Through 9/15 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0
(Summer Holiday) |  |  | SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
|  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Infiltration Schedule
INFIL_SCH_PNNL | fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
INFIL_Door_Opening_SCH | fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 1 | 0.144 | 0.144 | 0 | 0 | 0 | 0 | 0
|  |  | Sat, Sun, Hol, AllOtherDays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVAC Schedules
HVACOperationSchd | on/off | Through 12/31 | WD, SummerDesign, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
|  |  | Sat, Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FAN_SCH | AnyNumber | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
ReheatCoilAvailSched | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
CoolingCoilAvailSched | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
MinOA_MotorizedDamper_Sched | fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
|  |  | Sat, Sun, Hol, WinterDesign, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Sched | fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
| (°C) |  | SummerDesign, Sat, Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
CLGSETP_SCH | Temperature | Through 12/31 | WD | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44
| (°C) |  | SummerDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  |  | WinterDesign, Sat, Sun, Hol, Other | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
HTGSETP_SCH_SETBACk | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
(For mechanical room and bathroom) | (°C) |  | SummerDesign, Sat, Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
CLGSETP_SCH_SETUP | Temperature | Through 12/31 | WD | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
(For mechanical room and bathroom) | (°C) |  | SummerDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  |  | WinterDesign, Sat, Sun, Hol, Other | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
| (°C) | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
VAV-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
HTGSETP_SCH | Temperature | Through 12/31 | WD | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 64.04 | 68 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 60.08 | 60.08 | 60.08
| (°F) |  | SummerDesign, Sat, Sun, Hol, Other | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
|  |  | WinterDesign | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8
CLGSETP_SCH | Temperature | Through 12/31 | WD | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 82.04 | 78.08 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 84.992 | 84.992 | 84.992
| (°F) |  | SummerDesign | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2
|  |  | WinterDesign, Sat, Sun, Hol, Other | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992
HTGSETP_SCH_SETBACk | Temperature | Through 12/31 | WD | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
(For mechanical room and bathroom) | (°F) |  | SummerDesign, Sat, Sun, Hol, Other | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
|  |  | WinterDesign | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8
CLGSETP_SCH_SETUP | Temperature | Through 12/31 | WD | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992
(For mechanical room and bathroom) | (°F) |  | SummerDesign | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2
|  |  | WinterDesign, Sat, Sun, Hol, Other | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992 | 84.992
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4
| (°F) | Through 9/30 | All | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4
|  | Through 12/31 | All | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4
VAV-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04 | 55.04
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06 | 44.06
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8 | 60.8
Notes: | 1. For climate zones other than 1B, 2B, and 3B occupied cooling thermostat setpoints are maintained continuously (no setback). 2. These schedules reflect optimum start controls. For systems less than 10,000 cfm there is no optimal start and full occupied temperature setpoints begin two hours prior to occupancy instead of being ramped up incrementally beginning two hours prior to occupancy. 3. The schedules are also subject to changes in different models based on applicable code requrirements triggered by cllimate zone, system capacity, control type, or other criteria.

## SchedulePlots
Secondary School: Weekday Schedules